## Holding registers
Holding registers, Read/Write
User configuration
DEFINE | Address | Name | Values | Default | User level | Updated
HR_USER_CONFIG_CURRENT_SYSTEM_MODE | 1 | Current system mode | 0: Standby, 1:Building protection, 2:Economy, 3:Comfort | 0 | User | 2015-07-10
HR_USER_CONFIG_COMFORT_MODE_TEMPERATURE_SET_POINT | 2 | Comfort mode temperature Set Point | 160..300*0,1 °C | 210 | User | 2015-07-10
HR_USER_CONFIG_AIR_FLOW_BY_PERCENTS | 3 | Air flow control by percents | 0..100% | 0 | User | 2015-07-10
HR_USER_CONFIG_ECONOMY_MODE_TEMPERATURE_SET_POINT | 4 | Economy mode temperature Set Point | 0:Enegy saving, 160..300*0,1 °C | 180 | User | 2017-09-20
| 5 | Reserved
HR_USER_CONFIG_BUILDING_PROTECTION_MODE_TEMPERATURE_SET_POINT | 6 | Building protection mode temperature Set Point | 0:Enegy saving, 160..300*0,1 °C | 165 | User | 2017-09-20
HR_USER_CONFIG_REMOTE_MODE_SWITCH_TYPE | 7 | Remote mode switch type | 0: None, 1:Push button, 2:OnOff, 3:PIR | 2 | User | 2016-01-05
HR_USER_CONFIG_REMOTE_MODE_SWITCH_MODE | 8 | Remote mode switch mode | 0: Standby, 1:Building protection, 2:Economy, 3:Comfort | 0 | User | 2016-01-05
HR_USER_CONFIG_REMOTE_CUSTOM_FANS_SPEED_SWITCH_TYPE | 9 | Remote custom fans speed switch type | 0: None, 1: CUSTOM Push button, 2:OnOff CUSTOM, 3:BOOST Push button, 4:OnOff BOOST | 2 | User | 2016-01-05
HR_USER_CONFIG_REMOTE_CUSTOM_FANS_SPEED_SWITCH_SUPPLY_AIR_FLOW | 10 | Remote custom fans speed switch: supply air flow | 0..100% | 100 | User | 2016-01-05
HR_USER_CONFIG_REMOTE_CUSTOM_FANS_SPEED_SWITCH_EXTRACT_AIR_FLOW | 11 | Remote custom fans speed switch: extract air flow | 0..100% | 100 | User | 2016-01-05
HR_USER_CONFIG_FIRE_DAMPER_TESTING_HOUR | 12 | Fire damper testing hour | 0..23 | 6 | User | 2015-07-10
Reserved
HR_USER_CONFIG_INTENSIVE_AIR_FLOW_TIME_SET | 14 | Intensive air flow time set | 0-18000 s | 600 | User | 2015-10-30
HR_USER_CONFIG_WINTER_SUMMER_MODE | 15 | Winter/Summer mode | 0:Summer, 1:Winter, 2:By date, 3:By 3 days outside temp. average | 3 | User | 2016-01-05
HR_USER_CONFIG_WINTER_START_MONTH | 16 | Winter start month | 1-12 m. | 11 | User | 2015-12-08
HR_USER_CONFIG_WINTER_START_DAY | 17 | Winter start day | 1-31 d. | 1 | User | 2015-12-08
HR_USER_CONFIG_WINTER_END_MONTH | 18 | Winter end month | 1-12 m. | 3 | User | 2015-12-08
HR_USER_CONFIG_WINTER_END_DAY | 19 | Winter end day | 1-31 d. | 1 | User | 2015-12-08
HR_USER_CONFIG_WINTER_SUMMER_TEMPERATURE_LIMIT | 20 | Winter/Summer temperature limit | 0..30°C | 10 | User | 2015-12-08
HR_USER_RH_SUMMER_SET | 21 | Summer RH Set Point | 0..100% | 70 | User | 2016-08-30
HR_USER_RH_WINTER_SET | 22 | Winter RH Set Point | 0..100% | 50 | User | 2016-08-30
HR_USER_RH_BOOST_TIME | 23 | Too high RH boosting time | 1..600 min. | 30 | User | 2016-08-30
HR_USER_DRYNESS_PROT_SET | 24 | Dryness protection setpoint | 0..100% | 30 | User | 2017-11-29
HR_NIGHT_COOLING_START_HOURS | 25 | Night cooling: Start hours | 0-23 | 22 | User | 2015-11-26
HR_NIGHT_COOLING_START_MINS | 26 | Night cooling: Start minutes | 0-59 | 0 | User | 2015-11-26
HR_NIGHT_COOLING_STOP_HOURS | 27 | Night cooling: Stop hours | 0-23 | 6 | User | 2015-11-26
HR_NIGHT_COOLING_STOP_MINS | 28 | Night cooling: Stop minutes | 0-59 | 0 | User | 2015-11-26
HR_NIGHT_COOLING_START_EXTRACT | 29 | Night cooling: Extract air temperature for start | 130-300*0,1°C | 170 | User | 2015-11-26
HR_NIGHT_COOLING_STOP_EXTRACT | 30 | Night cooling: Extract air temperature for stop | 130-300*0,1°C | 140 | User | 2015-11-26
HR_NIGHT_COOLING_START_OUTDOOR | 31 | Night cooling: Outdoor temperature for stop | 0-300*0,1°C | 100 | User | 2015-11-26
HR_NIGHT_COOLING_SETPOINT | 32 | Night cooling: Supply air setpoint | 0-300*0,1°C | 150 | User | 2015-11-26
HR_POOL_DAY_START | 33 | Day start time | 0..23 h | 8 | User | 2017-11-29
HR_POOL_DAY_END | 34 | Day end time | 0..23 h | 21 | User | 2017-11-30
HR_POOL_OUTSIDE_T_LIMIT | 35 | Outside temperature limit | -30..50°C | 25 | User | 2017-11-30
HR_POOL_EXTRACT_RH_LOW_LIMIT | 36 | Extract RH low limit | 0..100% | 40 | User | 2017-11-30
HR_POOL_EXTRACT_RH_HI_LIMIT | 37 | Extract RH high limit | 0..100% | 64 | User | 2017-11-30
HR_USER_CONFIG_BUILDING_PROTECTION_MODE_RECIRCULATION_POSITION | 38 | Building protection mode recirculation position | (-1):Auto,0..1000*0.1% | -1 | User | 2018-09-21
HR_USER_CONFIG_ECONOMY_MODE_RECIRCULATION_POSITION | 39 | Economy mode recirculation position | (-1):Auto,0..1000*0.1% | -1 | User | 2018-09-21
HR_USER_CONFIG_COMFORT_MODE_RECIRCULATION_POSITION | 40 | Comfort mode recirculation position | (-1):Auto,0..1000*0.1% | -1 | User | 2018-09-21
HR_USER_CONFIG_WINTER_SUMMER_TSET_CORRECTION | 41 | Winter/Summer temperature setpoint correction | (-150)..150*0.1°C | 0 | User | 2018-09-21
Reserved
HR_USER_CONFIG_DATE_AND_TIME_SET_YEARS | 100 | Date and time set: Years | 0..99 | 0 | User | 2015-07-10
HR_USER_CONFIG_DATE_AND_TIME_SET_MONTH | 101 | Date and time set: Month | 1..12 | 0 | User | 2015-07-14
HR_USER_CONFIG_DATE_AND_TIME_SET_DAY | 102 | Date and time set: Day | 1..31 | 0 | User | 2015-07-10
| 103 | Reserved |  |  |  | 2015-11-26
HR_USER_CONFIG_DATE_AND_TIME_SET_HOURS | 104 | Date and time set: Hours | 0..23 | 0 | User | 2015-07-10
HR_USER_CONFIG_DATE_AND_TIME_SET_MINUTES | 105 | Date and time set: Minutes | 0..59 | 0 | User | 2015-07-10
HR_USER_CONFIG_DATE_AND_TIME_SET_SECONDS | 106 | Date and time set: Seconds | 0..59 | 0 | User | 2015-07-10
HR_USER_CONFIG_INTENSIVE_AIR_FLOW_TIME_LEFT | 107 | Intensive air flow time left | 0-18000 s | 0 | User | 2015-10-30
Reserved
HR_ADJUSTER_PASSWORD | 198 | Adjuster password input | 0-9999 | 1111 | User | 2015-07-10
HR_SERVICE_PASSWORD | 199 | Service password input | 0-9999 | 4444 | User | 2015-12-08
Reserved
HR_ALARM_A | 200 | Alarm A () | 0:no alarms, 1:alarm | 0 | User | 2015-07-10
HR_ALARM_B | 201 | Alarm B () | 0:no warning, 1:warning | 0 | User | 2015-07-10
HR_ALARMS_RESET | 202 | Alarms Reset | 0:Nothing, 1:Activate | 0 | User | 2015-07-10
HR_COOKING_HOOD_SPEED | 203 | Cooking hood Speed | (1,2,3,4 (4-th speed is boost and it is limited by time)) | 0 | User | 2015-07-10
HR_COOKING_HOOD_DAMPER | 204 | Cooking hood damper position | 0 :Opened, 1: Closed | 0 | User | 2015-11-23
HR_SHOW_ALARMS_ON_COOKING_HOOD | 205 | Show alarms on cooking hood | 0:Disabled, 1:Enabled | 1 | User | 2018-09-21
Reserved
Holidays Scheduler
DEFINE | Address | Name | Values | Default | User level | Updated
HR_HOLIDAYS_SCHEDULER_Interval_1 | 210 | Interval 1 | (-1):Deleted, 0: Disabled, 1:Enabled | -1 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_1_START_MONTH | 211 | Interval 1 Start Month | 1..12 | 0 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_1_START_DAY | 212 | Interval 1 Start Day | 1..31 | 0 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_1_START_HOUR | 213 | Interval 1 Start Hour | 0..23 | 0 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_1_END_MONTH | 214 | Interval 1 End Month | 1..12 | 0 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_1_END_DAY | 215 | Interval 1 End Day | 1..31 | 0 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_1_END_HOUR | 216 | Interval 1 End Hour | 0..23 | 0 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_1_INTERVAL_MODE | 217 | Interval 1 Mode | 0: Standby, 1:Building protection, 2:Economy, 3:Comfort | 2 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_Interval_2 | 218 | Interval 2 | (-1):Deleted, 0: Disabled, 1:Enabled | -1 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_2_START_MONTH | 219 | Interval 2 Start Month | 1..12 | 0 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_2_START_DAY | 220 | Interval 2 Start Day | 1..31 | 0 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_2_START_HOUR | 221 | Interval 2 Start Hour | 0..23 | 0 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_2_END_MONTH | 222 | Interval 2 End Month | 1..12 | 0 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_2_END_DAY | 223 | Interval 2 End Day | 1..31 | 0 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_2_END_HOUR | 224 | Interval 2 End Hour | 0..23 | 0 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_2_INTERVAL_MODE | 225 | Interval 2 Mode | 0: Standby, 1:Building protection, 2:Economy, 3:Comfort | 2 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_Interval_3 | 226 | Interval 3 | (-1):Deleted, 0: Disabled, 1:Enabled | -1 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_3_START_MONTH | 227 | Interval 3 Start Month | 1..12 | 0 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_3_START_DAY | 228 | Interval 3 Start Day | 1..31 | 0 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_3_START_HOUR | 229 | Interval 3 Start Hour | 0..23 | 0 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_3_END_MONTH | 230 | Interval 3 End Month | 1..12 | 0 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_3_END_DAY | 231 | Interval 3 End Day | 1..31 | 0 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_3_END_HOUR | 232 | Interval 3 End Hour | 0..23 | 0 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_3_INTERVAL_MODE | 233 | Interval 3 Mode | 0: Standby, 1:Building protection, 2:Economy, 3:Comfort | 2 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_Interval_4 | 234 | Interval 4 | (-1):Deleted, 0: Disabled, 1:Enabled | -1 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_4_START_MONTH | 235 | Interval 4 Start Month | 1..12 | 0 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_4_START_DAY | 236 | Interval 4 Start Day | 1..31 | 0 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_4_START_HOUR | 237 | Interval 4 Start Hour | 0..23 | 0 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_4_END_MONTH | 238 | Interval 4 End Month | 1..12 | 0 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_4_END_DAY | 239 | Interval 4 End Day | 1..31 | 0 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_4_END_HOUR | 240 | Interval 4 End Hour | 0..23 | 0 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_4_INTERVAL_MODE | 241 | Interval 4 Mode | 0: Standby, 1:Building protection, 2:Economy, 3:Comfort | 2 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_Interval_5 | 242 | Interval 5 | (-1):Deleted, 0: Disabled, 1:Enabled | -1 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_5_START_MONTH | 243 | Interval 5 Start Month | 1..12 | 0 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_5_START_DAY | 244 | Interval 5 Start Day | 1..31 | 0 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_5_START_HOUR | 245 | Interval 5 Start Hour | 0..23 | 0 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_5_END_MONTH | 246 | Interval 5 End Month | 1..12 | 0 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_5_END_DAY | 247 | Interval 5 End Day | 1..31 | 0 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_5_END_HOUR | 248 | Interval 5 End Hour | 0..23 | 0 | User | 2015-07-10
HR_HOLIDAYS_SCHEDULER_INTERVAL_5_INTERVAL_MODE | 249 | Interval 5 Mode | 0: Standby, 1:Building protection, 2:Economy, 3:Comfort | 2 | User | 2015-07-10
Weekly Scheduler
DEFINE | Address | Name | Values | Default | User level | Updated
HR_WEEKLY_SCHEDULER_EVENT_1 | 250 | Event 1 | (-1):Deleted, 0: Disabled, 1:Enabled | -1 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_1_SYSTEM_MODE | 251 | Event 1 Air flow | 0..4 / 0..100 % | 0 | User | 2017-04-27
HR_WEEKLY_SCHEDULER_EVENT_1_TEMPERATURE | 252 | Event 1 Temperature | (-1):Auto, 0:Energy saving, 160..300*0,1 °C | -1 | User | 2017-11-30
HR_WEEKLY_SCHEDULER_EVENT_1_WEEK_DAYS | 253 | Event 1 Week days | 0b00000000-0b01111111 (0b00000001 is Monday) | 0 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_1_TIME_HOURS | 254 | Event 1 Time (Hours) | 0-23 | 0 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_1_TIME_MINUTES | 255 | Event 1 Time (Minutes) | 0-59 | 0 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_2 | 256 | Event 2 | (-1):Deleted, 0: Disabled, 1:Enabled | -1 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_2_SYSTEM_MODE | 257 | Event 2 Air flow | 0..4 / 0..100 % | 0 | User | 2017-04-27
HR_WEEKLY_SCHEDULER_EVENT_2_TEMPERATURE | 258 | Event 2 Temperature | (-1):Auto, 0:Energy saving, 160..300*0,1 °C | -1 | User | 2017-11-30
HR_WEEKLY_SCHEDULER_EVENT_2_WEEK_DAYS | 259 | Event 2 Week days | 0b00000000-0b01111111 (0b00000001 is Monday) | 0 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_2_TIME_HOURS | 260 | Event 2 Time (Hours) | 0-23 | 0 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_2_TIME_MINUTES | 261 | Event 2 Time (Minutes) | 0-59 | 0 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_3 | 262 | Event 3 | (-1):Deleted, 0: Disabled, 1:Enabled | -1 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_3_SYSTEM_MODE | 263 | Event 3 Air flow | 0..4 / 0..100 % | 0 | User | 2017-04-27
HR_WEEKLY_SCHEDULER_EVENT_3_TEMPERATURE | 264 | Event 3 Temperature | (-1):Auto, 0:Energy saving, 160..300*0,1 °C | -1 | User | 2017-11-30
HR_WEEKLY_SCHEDULER_EVENT_3_WEEK_DAYS | 265 | Event 3 Week days | 0b00000000-0b01111111 (0b00000001 is Monday) | 0 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_3_TIME_HOURS | 266 | Event 3 Time (Hours) | 0-23 | 0 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_3_TIME_MINUTES | 267 | Event 3 Time (Minutes) | 0-59 | 0 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_4 | 268 | Event 4 | (-1):Deleted, 0: Disabled, 1:Enabled | -1 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_4_SYSTEM_MODE | 269 | Event 4 Air flow | 0..4 / 0..100 % | 0 | User | 2017-04-27
HR_WEEKLY_SCHEDULER_EVENT_4_TEMPERATURE | 270 | Event 4 Temperature | (-1):Auto, 0:Energy saving, 160..300*0,1 °C | -1 | User | 2017-11-30
HR_WEEKLY_SCHEDULER_EVENT_4_WEEK_DAYS | 271 | Event 4 Week days | 0b00000000-0b01111111 (0b00000001 is Monday) | 0 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_4_TIME_HOURS | 272 | Event 4 Time (Hours) | 0-23 | 0 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_4_TIME_MINUTES | 273 | Event 4 Time (Minutes) | 0-59 | 0 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_5 | 274 | Event 5 | (-1):Deleted, 0: Disabled, 1:Enabled | -1 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_5_SYSTEM_MODE | 275 | Event 5 Air flow | 0..4 / 0..100 % | 0 | User | 2017-04-27
HR_WEEKLY_SCHEDULER_EVENT_5_TEMPERATURE | 276 | Event 5 Temperature | (-1):Auto, 0:Energy saving, 160..300*0,1 °C | -1 | User | 2017-11-30
HR_WEEKLY_SCHEDULER_EVENT_5_WEEK_DAYS | 277 | Event 5 Week days | 0b00000000-0b01111111 (0b00000001 is Monday) | 0 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_5_TIME_HOURS | 278 | Event 5 Time (Hours) | 0-23 | 0 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_5_TIME_MINUTES | 279 | Event 5 Time (Minutes) | 0-59 | 0 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_6 | 280 | Event 6 | (-1):Deleted, 0: Disabled, 1:Enabled | -1 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_6_SYSTEM_MODE | 281 | Event 6 Air flow | 0..4 / 0..100 % | 0 | User | 2017-04-27
HR_WEEKLY_SCHEDULER_EVENT_6_TEMPERATURE | 282 | Event 6 Temperature | (-1):Auto, 0:Energy saving, 160..300*0,1 °C | -1 | User | 2017-11-30
HR_WEEKLY_SCHEDULER_EVENT_6_WEEK_DAYS | 283 | Event 6 Week days | 0b00000000-0b01111111 (0b00000001 is Monday) | 0 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_6_TIME_HOURS | 284 | Event 6 Time (Hours) | 0-23 | 0 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_6_TIME_MINUTES | 285 | Event 6 Time (Minutes) | 0-59 | 0 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_7 | 286 | Event 7 | (-1):Deleted, 0: Disabled, 1:Enabled | -1 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_7_SYSTEM_MODE | 287 | Event 7 Air flow | 0..4 / 0..100 % | 0 | User | 2017-04-27
HR_WEEKLY_SCHEDULER_EVENT_7_TEMPERATURE | 288 | Event 7 Temperature | (-1):Auto, 0:Energy saving, 160..300*0,1 °C | -1 | User | 2017-11-30
HR_WEEKLY_SCHEDULER_EVENT_7_WEEK_DAYS | 289 | Event 7 Week days | 0b00000000-0b01111111 (0b00000001 is Monday) | 0 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_7_TIME_HOURS | 290 | Event 7 Time (Hours) | 0-23 | 0 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_7_TIME_MINUTES | 291 | Event 7 Time (Minutes) | 0-59 | 0 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_8 | 292 | Event 8 | (-1):Deleted, 0: Disabled, 1:Enabled | -1 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_8_SYSTEM_MODE | 293 | Event 8 Air flow | 0..4 / 0..100 % | 0 | User | 2017-04-27
HR_WEEKLY_SCHEDULER_EVENT_8_TEMPERATURE | 294 | Event 8 Temperature | (-1):Auto, 0:Energy saving, 160..300*0,1 °C | -1 | User | 2017-11-30
HR_WEEKLY_SCHEDULER_EVENT_8_WEEK_DAYS | 295 | Event 8 Week days | 0b00000000-0b01111111 (0b00000001 is Monday) | 0 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_8_TIME_HOURS | 296 | Event 8 Time (Hours) | 0-23 | 0 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_8_TIME_MINUTES | 297 | Event 8 Time (Minutes) | 0-59 | 0 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_9 | 298 | Event 9 | (-1):Deleted, 0: Disabled, 1:Enabled | -1 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_9_SYSTEM_MODE | 299 | Event 9 Air flow | 0..4 / 0..100 % | 0 | User | 2017-04-27
HR_WEEKLY_SCHEDULER_EVENT_9_TEMPERATURE | 300 | Event 9 Temperature | (-1):Auto, 0:Energy saving, 160..300*0,1 °C | -1 | User | 2017-11-30
HR_WEEKLY_SCHEDULER_EVENT_9_WEEK_DAYS | 301 | Event 9 Week days | 0b00000000-0b01111111 (0b00000001 is Monday) | 0 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_9_TIME_HOURS | 302 | Event 9 Time (Hours) | 0-23 | 0 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_9_TIME_MINUTES | 303 | Event 9 Time (Minutes) | 0-59 | 0 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_10 | 304 | Event 10 | (-1):Deleted, 0: Disabled, 1:Enabled | -1 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_10_SYSTEM_MODE | 305 | Event 10 Air flow | 0..4 / 0..100 % | 0 | User | 2017-04-27
HR_WEEKLY_SCHEDULER_EVENT_10_TEMPERATURE | 306 | Event 10 Temperature | (-1):Auto, 0:Energy saving, 160..300*0,1 °C | -1 | User | 2017-11-30
HR_WEEKLY_SCHEDULER_EVENT_10_WEEK_DAYS | 307 | Event 10 Week days | 0b00000000-0b01111111 (0b00000001 is Monday) | 0 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_10_TIME_HOURS | 308 | Event 10 Time (Hours) | 0-23 | 0 | User | 2015-07-10
HR_WEEKLY_SCHEDULER_EVENT_10_TIME_MINUTES | 309 | Event 10 Time (Minutes) | 0-59 | 0 | User | 2015-07-10
Reserved
Alarm History (50 events)
DEFINE | Address | Name | Values | Default | User level | Updated
HR_ALARM_HISTORY_PAGE | 330 | Page | 1..5 | 1 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_1_YEARS | 331 | Event (1*Page) Years | 0..99 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_1_MONTH | 332 | Event (1*Page) Month | 1..12 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_1_DAY | 333 | Event (1*Page) Day | 1..31 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_1_HOURS | 334 | Event (1*Page) Hours | 0..23 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_1_MINUTES | 335 | Event (1*Page) Minutes | 0..59 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_1_MESSAGE_ID | 336 | Event (1*Page) Message ID | 0..255 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_2_YEARS | 337 | Event (2*Page) Years | 0..99 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_2_MONTH | 338 | Event (2*Page) Month | 1..12 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_2_DAY | 339 | Event (2*Page) Day | 1..31 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_2_HOURS | 340 | Event (2*Page) Hours | 0..23 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_2_MINUTES | 341 | Event (2*Page) Minutes | 0..59 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_2_MESSAGE_ID | 342 | Event (2*Page) Message ID | 0..255 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_3_YEARS | 343 | Event (3*Page) Years | 0..99 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_3_MONTH | 344 | Event (3*Page) Month | 1..12 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_3_DAY | 345 | Event (3*Page) Day | 1..31 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_3_HOURS | 346 | Event (3*Page) Hours | 0..23 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_3_MINUTES | 347 | Event (3*Page) Minutes | 0..59 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_3_MESSAGE_ID | 348 | Event (3*Page) Message ID | 0..255 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_4_YEARS | 349 | Event (4*Page) Years | 0..99 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_4_MONTH | 350 | Event (4*Page) Month | 1..12 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_4_DAY | 351 | Event (4*Page) Day | 1..31 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_4_HOURS | 352 | Event (4*Page) Hours | 0..23 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_4_MINUTES | 353 | Event (4*Page) Minutes | 0..59 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_4_MESSAGE_ID | 354 | Event (4*Page) Message ID | 0..255 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_5_YEARS | 355 | Event (5*Page) Years | 0..99 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_5_MONTH | 356 | Event (5*Page) Month | 1..12 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_5_DAY | 357 | Event (5*Page) Day | 1..31 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_5_HOURS | 358 | Event (5*Page) Hours | 0..23 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_5_MINUTES | 359 | Event (5*Page) Minutes | 0..59 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_5_MESSAGE_ID | 360 | Event (5*Page) Message ID | 0..255 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_6_YEARS | 361 | Event (6*Page) Years | 0..99 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_6_MONTH | 362 | Event (6*Page) Month | 1..12 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_6_DAY | 363 | Event (6*Page) Day | 1..31 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_6_HOURS | 364 | Event (6*Page) Hours | 0..23 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_6_MINUTES | 365 | Event (6*Page) Minutes | 0..59 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_6_MESSAGE_ID | 366 | Event (6*Page) Message ID | 0..255 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_7_YEARS | 367 | Event (7*Page) Years | 0..99 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_7_MONTH | 368 | Event (7*Page) Month | 1..12 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_7_DAY | 369 | Event (7*Page) Day | 1..31 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_7_HOURS | 370 | Event (7*Page) Hours | 0..23 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_7_MINUTES | 371 | Event (7*Page) Minutes | 0..59 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_7_MESSAGE_ID | 372 | Event (7*Page) Message ID | 0..255 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_8_YEARS | 373 | Event (8*Page) Years | 0..99 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_8_MONTH | 374 | Event (8*Page) Month | 1..12 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_8_DAY | 375 | Event (8*Page) Day | 1..31 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_8_HOURS | 376 | Event (8*Page) Hours | 0..23 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_8_MINUTES | 377 | Event (8*Page) Minutes | 0..59 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_8_MESSAGE_ID | 378 | Event (8*Page) Message ID | 0..255 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_9_YEARS | 379 | Event (9*Page) Years | 0..99 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_9_MONTH | 380 | Event (9*Page) Month | 1..12 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_9_DAY | 381 | Event (9*Page) Day | 1..31 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_9_HOURS | 382 | Event (9*Page) Hours | 0..23 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_9_MINUTES | 383 | Event (9*Page) Minutes | 0..59 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_9_MESSAGE_ID | 384 | Event (9*Page) Message ID | 0..255 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_10_YEARS | 385 | Event (10*Page) Years | 0..99 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_10_MONTH | 386 | Event (10*Page) Month | 1..12 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_10_DAY | 387 | Event (10*Page) Day | 1..31 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_10_HOURS | 388 | Event (10*Page) Hours | 0..23 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_10_MINUTES | 389 | Event (10*Page) Minutes | 0..59 | 0 | User | 2015-07-10
HR_ALARM_HISTORY_EVENT_10_MESSAGE_ID | 390 | Event (10*Page) Message ID | 0..255 | 0 | User | 2015-07-10
Reserved
Manual control
DEFINE | Address | Name | Values | Default | User level | Updated
HR_MANUAL_CONTROL_HEATER_CONTROL_OUTPUT | 400 | Heater control output | (-1):Auto , 0..1000*0,1% | -1 | Adjuster | 2015-07-10
HR_MANUAL_CONTROL_HEATER_POWER_LINE_CIRCULATION_PUMP | 401 | Heater power line/circulation pump | (-1):Auto , 0:Off ,1:On | -1 | Adjuster | 2015-07-10
HR_MANUAL_CONTROL_PREHEATER_CONTROL_OUTPUT | 402 | Preater control output | (-1):Auto , 0..1000*0,1% | -1 | Adjuster | 2015-07-10
HR_MANUAL_CONTROL_PREHEATER_POWER_LINE_CIRCULATION_PUMP | 403 | Pre-heater power line/circulation pump | (-1):Auto , 0:Off ,1:On | -1 | Adjuster | 2015-07-10
HR_MANUAL_CONTROL_SUPPLY_CONTROL_OUTPUT | 404 | Supply fan control output | (-1):Auto , 0..1000*0,1% | -1 | Adjuster | 2015-07-10
HR_MANUAL_CONTROL_EXTRACT_CONTROL_OUTPUT | 405 | Extract fan control output | (-1):Auto , 0..1000*0,1% | -1 | Adjuster | 2015-07-10
HR_MANUAL_POWER_FANS_POWER_LINE | 406 | Fans power line | (-1):Auto , 0:Off ,1:On | -1 | Adjuster | 2015-07-10
HR_MANUAL_CONTROL_HYDRONIC_CONTROL_OUTPUT | 407 | Hydronic cooler control output | (-1):Auto , 0..1000*0,1% | -1 | Adjuster | 2015-12-08
HR_MANUAL_CIRCULATION_HYDRONIC_CIRCULATION_PUMP | 408 | Hydronic cooler circulation pump | (-1):Auto , 0:Off ,1:On | -1 | Adjuster | 2015-12-08
HR_MANUAL_SUPPLY_RECIRCULATION_DAMPER_POSITION | 409 | Supply recirculation damper position | (-1):Auto , 0..1000*0,1% | -1 | Adjuster | 2017-11-29
HR_MANUAL_SUPPLY_RECIRCULATION_OPEN_OUTPUT | 410 | Supply recirculation damper open output | (-1):Auto , 0:Off ,1:On | -1 | Adjuster | 2017-11-29
HR_MANUAL_SUPPLY_RECIRCULATION_CLOSE_OUTPUT | 411 | Supply recirculation damper close output | (-1):Auto , 0:Off ,1:On | -1 | Adjuster | 2017-11-29
HR_MANUAL_CONTROL_EXTRACT_DAMPER_POSITION | 412 | Extract air damper position | (-1):Auto , 0..1000*0,1% | -1 | Adjuster | 2018-03-28
HR_MANUAL_CONTROL_EXTRACT_DAMPER_OPEN_OUTPUT | 413 | Extract air damper open output | (-1):Auto , 0:Off ,1:On | -1 | Adjuster | 2018-03-28
HR_MANUAL_CONTROL_EXTRACT_DAMPER_CLOSE_OUTPUT | 414 | Extract air damper close output | (-1):Auto , 0:Off ,1:On | -1 | Adjuster | 2018-03-28
HR_MANUAL_BYPASS_BYPASS_BYPASS_POSITION | 415 | Bypass position | (-1):Auto , 0..1000*0,1% | -1 | Adjuster | 2015-07-10
HR_MANUAL_OPEN_BYPASS_OPEN_OUTPUT | 416 | Bypass open output | (-1):Auto , 0:Off ,1:On | -1 | Adjuster | 2015-07-10
HR_MANUAL_CLOSE_BYPASS_CLOSE_OUTPUT | 417 | Bypass close output | (-1):Auto , 0:Off ,1:On | -1 | Adjuster | 2015-07-10
HR_MANUAL_CONTROL_ROTOR_CONTROL_OUTPUT | 418 | Rotor control output | (-1):Auto , 0..1000*0,1% | -1 | Adjuster | 2015-07-10
HR_MANUAL_ROTOR_ROTOR_ROTOR_ON | 419 | Rotor ON | (-1):Auto , 0:Off ,1:On | -1 | Adjuster | 2015-07-10
HR_MANUAL_COOLER_DX_COOLER_CONTROL_OUTPUT | 420 | DX cooler control output | (-1):Auto , 0..1000*0,1% | -1 | Adjuster | 2016-01-07
HR_MANUAL_POWER_DX_POWER_LINE | 421 | DX cooler power line | (-1):Auto , 0:Off ,1:On | -1 | Adjuster | 2015-07-10
HR_MANUAL_DAMPER_FIRE_DAMPER_POSITION | 422 | Fire damper position | (-1):Auto , 0..1000*0,1% | -1 | Adjuster | 2015-07-10
HR_MANUAL_OPEN_FIRE_OPEN_OUTPUT | 423 | Fire damper open output | (-1):Auto , 0:Off ,1:On | -1 | Adjuster | 2015-07-10
HR_MANUAL_CLOSE_FIRE_CLOSE_OUTPUT | 424 | Fire damper close output | (-1):Auto , 0:Off ,1:On | -1 | Adjuster | 2015-07-10
HR_MANUAL_CONTROL_BOX_HEATER_OUTPUT | 425 | Controller cabinet heater/fan output | (-1):Auto , 0:Off ,1:On | -1 | Adjuster | 2015-12-08
HR_MANUAL_INDICATION_WORKING_INDICATION_OUTPUT | 426 | Working indication output | (-1):Auto , 0:Off ,1:On | -1 | Adjuster | 2015-07-10
HR_MANUAL_INDICATION_ALARM_INDICATION_OUTPUT | 427 | Alarm indication output | (-1):Auto , 0:Off ,1:On | -1 | Adjuster | 2015-07-10
HR_MANUAL_DX_COOLER_REVERSE | 428 | DX cooler reverse | (-1):Auto , 0:Off ,1:On | -1 | Adjuster | 2015-07-10
HR_MANUAL_DX_COOLER_DEFROST | 429 | DX defrost output | (-1):Auto , 0:Off ,1:On | -1 | Adjuster | 2017-11-29
HR_MANUAL_OUTSIDE_RECIRCULATION_DAMPER_POSITION | 430 | Outside recirculation damper position | (-1):Auto , 0..1000*0,1% | -1 | Adjuster | 2017-11-30
HR_MANUAL_OUTSIDE_RECIRCULATION_OPEN_OUTPUT | 431 | Outside recirculation damper open output | (-1):Auto , 0:Off ,1:On | -1 | Adjuster | 2017-12-01
HR_MANUAL_OUTSIDE_RECIRCULATION_CLOSE_OUTPUT | 432 | Outside recirculation damper close output | (-1):Auto , 0:Off ,1:On | -1 | Adjuster | 2017-12-02
HR_MANUAL_CONTROL_SUPPLY_DAMPER_POSITION | 433 | Supply air damper position | (-1):Auto , 0..1000*0,1% | -1 | Adjuster | 2018-03-28
HR_MANUAL_CONTROL_SUPPLY_DAMPER_OPEN_OUTPUT | 434 | Supply air damper open output | (-1):Auto , 0:Off ,1:On | -1 | Adjuster | 2018-03-28
HR_MANUAL_CONTROL_SUPPLY_DAMPER_CLOSE_OUTPUT | 435 | Supply air damper close output | (-1):Auto , 0:Off ,1:On | -1 | Adjuster | 2018-03-28
HR_MANUAL_CONTROL_COOKERHOOD_DAMPER_OPEN_OUTPUT | 436 | CookerHood damper open | (-1):Auto , 0:Off ,1:On | -1 | Adjuster | 2026-04-22
HR_MANUAL_CONTROL_COOKERHOOD_DAMPER_CLOSE_OUTPUT | 437 | CookerHood damper close | (-1):Auto , 0:Off ,1:On | -1 | Adjuster | 2026-04-22
HR_MANUAL_CONTROL_COOKERHOOD_LIGHTING_OUTPUT | 438 | CookerHood lighting output | (-1):Auto , 0:Off ,1:On | -1 | Adjuster | 2026-04-22
Reserved
Air flow adjustment
DEFINE | Address | Name | Values | Default | User level | Updated
HR_AIR_FLOW_1_SUPPLY | 450 | 1 Supply air flow (%) | 1..2 Supply air flow (%) | 300 | Adjuster | 2015-07-10
HR_AIR_FLOW_2_SUPPLY | 451 | 2 Supply air flow (%) | 1 Supply air flow (%)..3 Supply air flow (%) | 500 | Adjuster | 2015-07-10
HR_AIR_FLOW_3_SUPPLY | 452 | 3 Supply air flow (%) | 2 Supply air flow (%)..4 Supply air flow (%) | 700 | Adjuster | 2015-07-10
HR_AIR_FLOW_4_SUPPLY | 453 | 4 Supply air flow (%) | 3 Supply air flow (%)..1000*0,1% | 1000 | Adjuster | 2015-07-10
| 454 | Reserved
HR_AIR_FLOW_1_EXTRACT | 456 | 1 Extract air flow (%) | 1..2 Extract air flow (%) | 300 | Adjuster | 2015-07-10
HR_AIR_FLOW_2_EXTRACT | 457 | 2 Extract air flow (%) | 1 Extract air flow (%)..3 Extract air flow (%) | 500 | Adjuster | 2015-07-10
HR_AIR_FLOW_3_EXTRACT | 458 | 3 Extract air flow (%) | 2 Extract air flow (%)..4 Extract air flow (%) | 700 | Adjuster | 2015-07-10
HR_AIR_FLOW_4_EXTRACT | 459 | 4 Extract air flow (%) | 3 Extract air flow (%)..1000*0,1% | 1000 | Adjuster | 2015-07-10
| 460 | Reserved
HR_AIR_FLOW_EXTRACT_SUPPLY_DIFERENCE | 462 | Extract fan speed from supply fan speed diference(%) | (-1000)..1000*0,1% | 0 | Adjuster | 2015-12-10
Reserved
HR_TACHO_PULSES_PER_REVOLUTION | 464 | Tacho pulses per revolution | 1 - 10 impulses | 1 | Adjuster | 2015-12-03
Reserved
Sensor Corrections
DEFINE | Address | Name | Values | Default | User level | Updated
HR_SENSORS_SUPPLY_AIR_TEMPERATURE_SENSOR_CORRECTION | 480 | Supply air temperature sensor correction | -1000..1000*0,1 | 0 | Adjuster | 2017-04-27
HR_SENSORS_EXTRACT_AIR_TEMPERATURE_SENSOR_CORRECTION | 481 | Extract air temperature sensor correction | -1000..1000*0,1 | 0 | Adjuster | 2017-04-27
HR_SENSORS_EXHAUST_AIR_TEMPERATURE_SENSOR_CORRECTION | 482 | Exhaust air temperature sensor correction | -1000..1000*0,1 | 0 | Adjuster | 2017-04-27
HR_SENSORS_OUTDOOR_AIR_TEMPERATURE_SENSOR_CORRECTION | 483 | Outdoor air temperature sensor correction | -1000..1000*0,1 | 0 | Adjuster | 2017-04-27
HR_SENSORS_HYDRONIC_HEATER_WATER_TEMPERATURE_SENSOR_CORRECTION | 484 | Hydronic heater water temperature sensor correction | -1000..1000*0,1 | 0 | Adjuster | 2017-04-27
HR_SENSORS_HYDRONIC_PREHEATER_WATER_TEMPERATURE_SENSOR_CORRECTION | 485 | Hydronic preheater water temperature sensor correction | -1000..1000*0,1 | 0 | Adjuster | 2017-04-27
HR_SENSORS_HYDRONIC_COOLER_WATER_TEMPERATURE_SENSOR_CORRECTION | 486 | Hydronic cooler water temperature sensor correction | -1000..1000*0,1 | 0 | Adjuster | 2017-04-27
HR_SENSORS_CONTROL_BOX_TEMPERATURE_SENSOR_CORRECTION | 487 | Control box temperature sensor correction | -1000..1000*0,1 | 0 | Adjuster | 2017-04-27
HR_SENSORS_AIR_QUALITY_SENSOR_1_CORRECTION | 488 | Air quality sensor 1 correction | -1000..1000*0,1 | 0 | Adjuster | 2017-04-27
HR_SENSORS_AIR_QUALITY_SENSOR_2_CORRECTION | 489 | Air quality sensor 2 correction | -1000..1000*0,1 | 0 | Adjuster | 2017-04-27
HR_SENSORS_RESERVED_VDC | 490 | Reserved vdc correction | -1000..1000*0,1 | 0 | Adjuster | 2017-04-27
HR_SENSORS_AFTER_HX_TEMPERATURE_SENSOR_CORRECTION | 491 | After heat exchanger temperature sensor correction | -1000..1000*0,1 | 0 | Adjuster | 2019-03-14
PID's adjustment
DEFINE | Address | Name | Values | Default | User level | Updated
HR_PIDS_HEATER_P | 500 | Heater P coef. | 0..1000 | 30 | Adjuster | 2015-11-26
HR_PIDS_HEATER_I | 501 | Heater I coef. | 0..1000 | 60 | Adjuster | 2015-11-26
HR_PIDS_HEATER_D | 502 | Heater D coef. | 0..1000 | 0 | Adjuster | 2015-11-26
HR_PIDS_PREHEATER_P | 503 | Pre-heater P coef. | 0..1000 | 30 | Adjuster | 2015-11-26
HR_PIDS_PREHEATER_I | 504 | Pre-heater I coef. | 0..1000 | 60 | Adjuster | 2015-11-26
HR_PIDS_PREHEATER_D | 505 | Pre-heater D coef. | 0..1000 | 0 | Adjuster | 2015-11-26
HR_PIDS_FANS_PRESURE_P | 506 | Fans presure P coef. | 0..1000 | 30 | Adjuster | 2015-11-26
HR_PIDS_FANS_PRESURE_I | 507 | Fans presure I coef. | 0..1000 | 60 | Adjuster | 2015-11-26
HR_PIDS_FANS_PRESURE_D | 508 | Fans presure D coef. | 0..1000 | 0 | Adjuster | 2015-11-26
HR_PIDS_HEAT_EXCHANGER_P | 509 | Heat exchanger P coef. | 0..1000 | 30 | Adjuster | 2015-11-26
HR_PIDS_HEAT_EXCHANGER_I | 510 | Heat exchanger I coef. | 0..1000 | 60 | Adjuster | 2015-11-26
HR_PIDS_HEAT_EXCHANGER_D | 511 | Heat exchanger D coef. | 0..1000 | 0 | Adjuster | 2015-11-26
HR_PIDS_HYDRONIC_COOLER_P | 512 | Hydronic cooler P coef. | 0..1000 | 30 | Adjuster | 2015-12-08
HR_PIDS_HYDRONIC_COOLER_I | 513 | Hydronic cooler I coef. | 0..1000 | 60 | Adjuster | 2015-12-08
HR_PIDS_HYDRONIC_COOLER_D | 514 | Hydronic cooler D coef. | 0..1000 | 0 | Adjuster | 2015-12-08
HR_PIDS_FANS_BY_TEMPERATURE_P | 515 | Fans by temperature P coef. | 0..1000 | 30 | Adjuster | 2015-11-26
HR_PIDS_FANS_BY_TEMPERATURE_I | 516 | Fans by temperature I coef. | 0..1000 | 60 | Adjuster | 2015-11-26
HR_PIDS_FANS_BY_TEMPERATURE_D | 517 | Fans by temperature D coef. | 0..1000 | 0 | Adjuster | 2015-11-26
HR_PIDS_RECIRC_TEMPERATURE_P | 518 | Recirculation by temperature P coef. | 0..1000 | 30 | Adjuster | 2015-11-26
HR_PIDS_RECIRC_TEMPERATURE_I | 519 | Recirculation by temperature I coef. | 0..1000 | 60 | Adjuster | 2015-11-26
HR_PIDS_RECIRC_TEMPERATURE_D | 520 | Recirculation by temperature D coef. | 0..1000 | 0 | Adjuster | 2015-11-26
HR_PIDS_DX_COOLER_P | 521 | DX cooler P coef. | 0..1000 | 30 | Adjuster | 2018-03-01
HR_PIDS_DX_COOLER_I | 522 | DX cooler I coef. | 0..1000 | 60 | Adjuster | 2018-03-01
HR_PIDS_DX_COOLER_D | 523 | DX cooler D coef. | 0..1000 | 0 | Adjuster | 2018-03-01
Reserved
Service configuration
DEFINE | Address | Name | Values | Default | User level | Updated
HR_SERVICE_HEATER_TYPE | 600 | Heater type | 0:None, 1:Electrical 0-10, 2:Electrical On/Off, 3:Hydronic | 0 | Service | 2015-12-08
HR_SERVICE_HEATER_ALARM_ACTION | 601 | Heater alarm action | 0:Stop system, 1:Intensive ventiliation | 1 | Service | 2015-07-10
HR_SERVICE_ELECTRICAL_HEATER_COOLING_TIME | 602 | Electrical heater cooling time | 0..100 (seconds) | 30 | Service | 2015-07-10
HR_SERVICE_HYDRONIC_HEATER_PREPARING_TIME | 603 | Hydronic heater preparing time | 0..600 (seconds) | 30 | Service | 2017-01-24
HR_SERVICE_HYDRONIC_HEATER_FROST_TEMPERATURE | 604 | Hydronic heater frost temperature | (-30)..10°C | 5 | Service | 2015-12-08
HR_SERVICE_PREHEATER_TYPE | 605 | Pre-heater type | 0:None, 1:Electrical 0-10, 2:Electrical On/Off, 3:Hydronic | 0 | Service | 2015-12-08
HR_SERVICE_PREHEATER_ALARM_ACTION | 606 | Pre-heater alarm action | 0:Stop system, 1:Intensive ventiliation | 1 | Service | 2015-07-10
HR_SERVICE_HEATER_PWM_TIME | 607 | Heater PWM time | 0..300 | 60 | Service | 2015-07-10
HR_SERVICE_PREHEATER_PWM_TIME | 608 | Pre-heater PWM time | 0..300 | 60 | Service | 2015-07-10
HR_SERVICE_HYDRONIC_PREHEATER_FROST_TEMPERATURE | 609 | Hydronic pre-heater frost temperature | (-30)..10°C | 5 | Service | 2015-12-16
HR_SERVICE_ANTIFROST_DEACTIVATION_DIF | 610 | Antifrost deactivation temperature difference | 0..100*0,1 °C | 20 | Service | 2015-07-10
HR_SERVICE_ANTIFROST_OUTSIDE_SET | 611 | Use outside frost temperature | 0:Not Active, -1 .. -400*0,1 °C | -20 | Service | 2018-03-01
HR_SERVICE_FANS_TYPE | 612 | Fans type | 0: EC, 1:AC | 0 | Service | 2015-07-10
HR_SERVICE_FANS_CONTROL_TYPE | 613 | Fans control type | 0: Percents, 1:Pressure, 2:Air flow | 0 | Service | 2015-07-10
HR_SERVICE_K_FACTOR_SUPPLY | 614 | Supply K factor | 0..10000*0.1 | 0 | Service | 2015-07-10
HR_SERVICE_MAXIMAL_AIR_FLOW_PRESSURE | 615 | Maximum air flow pressure (Pa) | 0..30000 Pa | 0 | Service | 2017-02-01
HR_SERVICE_MAXIMAL_AIR_FLOW | 616 | Maximum air flow (m3/h) | 0..30000 m3/h | 0 | Service | 2017-02-01
HR_SERVICE_MAXIMAL_SUPPLY_FAN_VOLTAGE | 617 | Maximum fan voltage (Volts) | 0..1000 *0.01 Volts | 1000 | Service | 2017-02-01
Reserved
HR_SERVICE_MINIMAL_FAN_VOLTAGE | 620 | Minimum fan voltage (Volts) | 0..1000 *0.01 Volts | 200 | Service | 2017-02-01
HR_SERVICE_HEAT_EXCHANGER_TYPE | 621 | Heat exchanger type | 0: None, 1:Plate, 2:Rotor | 1 | Service | 2015-07-10
HR_SERVICE_BYPASS_OPEN_TIME | 622 | Bypass open time | 0..255 (seconds) | 60 | Service | 2015-07-10
HR_SERVICE_ROTOR_OUTPUT_THRESHOLD | 623 | Rotor output threshold | 0..100% | 20 | Service | 2015-07-10
HR_SERVICE_HYDRONIC_COOLER_FROST_TEMPERATURE | 624 | Hydronic cooler frost temperature | (-30)..10°C | 5 | Service | 2015-12-08
HR_SERVICE_DX_COOLER_MINIMAL_OFF_TIME | 625 | DX cooler minimal Off time | 1..30 min. | 5 | Service | 2015-07-10
HR_SERVICE_SUPPLY_AIR_TEMPERATURE_SENSOR_TYPE | 626 | Supply air temperature sensor type | 0:None,1:Remote, 2:NTC 10K 3997, 2750...5000 (Custom NTC beta) | 2 | Service | 2017-09-18
HR_SERVICE_EXTRACT_AIR_TEMPERATURE_SENSOR_TYPE | 627 | Extract air temperature sensor type | 0:None,1:Remote, 2:NTC 10K 3997, 2750...5000 (Custom NTC beta) | 2 | Service | 2017-09-18
HR_SERVICE_EXHAUST_AIR_TEMPERATURE_SENSOR_TYPE | 628 | Exhaust air temperature sensor type | 0:None,1:Remote, 2:NTC 10K 3997, 2750...5000 (Custom NTC beta) | 2 | Service | 2017-09-18
HR_SERVICE_OUTDOOR_AIR_TEMPERATURE_SENSOR_TYPE | 629 | Outdoor air temperature sensor type | 0:None,1:Remote, 2:NTC 10K 3997, 2750...5000 (Custom NTC beta) | 2 | Service | 2017-09-18
HR_SERVICE_HYDRONIC_HEATER_WATER_TEMPERATURE_SENSOR_TYPE | 630 | Hydronic heater water temperature sensor type | 0:None,1:Remote, 2:NTC 10K 3997, 2750...5000 (Custom NTC beta) | 2 | Service | 2017-09-18
HR_SERVICE_HYDRONIC_PREHEATER_WATER_TEMPERATURE_SENSOR_TYPE | 631 | Hydronic pre-heater water temperature sensor type | 0:None,1:Remote, 2:NTC 10K 3997, 2750...5000 (Custom NTC beta) | 2 | Service | 2017-09-18
HR_SERVICE_HYDRONIC_COOLER_WATER_TEMPERATURE_SENSOR_TYPE | 632 | Hydronic cooler water temperature sensor type | 0:None,1:Remote, 2:NTC 10K 3997, 2750...5000 (Custom NTC beta) | 2 | Service | 2017-09-18
HR_SERVICE_CONTROL_BOX_TEMPERATURE_SENSOR_TYPE | 633 | Controller cabinet temperature sensor type | 0:None,1:Remote, 2:NTC 10K 3997, 2750...5000 (Custom NTC beta) | 2 | Service | 2017-09-18
HR_SERVICE_SUPPLY_AIR_TEMPERATURE_SENSOR_ALARM_ACTION | 634 | Supply air temperature sensor alarm action | 0: None, 1:Stop system, 2:Emergency run | 1 | Service | 2015-07-10
HR_SERVICE_EXTRACT_AIR_TEMPERATURE_SENSOR_ALARM_ACTION | 635 | Extract air temperature sensor alarm action | 0: None, 1:Stop system, 2:Emergency run | 1 | Service | 2015-07-10
HR_SERVICE_EXHAUST_AIR_TEMPERATURE_SENSOR_ALARM_ACTION | 636 | Exhaust air temperature sensor alarm action | 0: None, 1:Stop system, 2:Emergency run | 1 | Service | 2015-07-10
HR_SERVICE_OUTDOOR_AIR_TEMPERATURE_SENSOR_ALARM_ACTION | 637 | Outdoor air temperature sensor alarm action | 0: None, 1:Stop system, 2:Emergency run | 1 | Service | 2017-04-27
HR_SERVICE_HYDRONIC_HEATER_WATER_TEMPERATURE_SENSOR_ALARM_ACTION | 638 | Hydronic heater water temperature sensor alarm action | 0: None, 1:Stop system, 2:Emergency run | 1 | Service | 2016-01-05
HR_SERVICE_HYDRONIC_PREHEATER_WATER_TEMPERATURE_SENSOR_ALARM_ACTION | 639 | Hydronic pre-heater water temperature sensor alarm action | 0: None, 1:Stop system, 2:Emergency run | 1 | Service | 2016-01-05
HR_SERVICE_HYDRONIC_COOLER_WATER_TEMPERATURE_SENSOR_ALARM_ACTION | 640 | Hydronic cooler water temperature sensor alarm action | 0: None, 1:Stop system, 2:Emergency run | 1 | Service | 2016-01-05
HR_SERVICE_CONTROL_BOX_TEMPERATURE_SENSOR_ALARM_ACTION | 641 | Controller cabinet temperature sensor alarm action | 0: None, 1:Stop system, 2:Emergency run | 0 | Service | 2015-12-08
HR_SERVICE_FIRE_PROTECTION_ACTION | 642 | Fire protection mode | 0: Stop system, 1:Supply air, 2:Extract air, 3:Both | 0 | Service | 2015-12-08
HR_SERVICE_FIRE_PROTECTION_INPUT_TIMEOUT | 643 | Fire protection input timeout | 0..100 (seconds) | 10 | Service | 2015-07-10
HR_SERVICE_FIRE_DAMPER_TYPE | 644 | Fire damper type | 0:None,1:One switch, 2:Two swithes | 0 | Service | 2015-07-10
HR_SERVICE_FIRE_DAMPER_OPEN_TIME | 645 | Fire damper open time | 0..255 (seconds) | 60 | Service | 2015-07-10
HR_SERVICE_FIRE_DAMPER_TESTING_DAYS_INTERVAL | 646 | Fire damper testing days interval | 1..120 | 30 | Service | 2015-07-10
HR_SERVICE_RECIRCULATION_DAMPER_OPEN_TIME | 647 | Recirculation damper open time | 0..255 (seconds) | 60 | Service | 2015-07-10
HR_SERVICE_EXTRACT_DAMPER_TYPE | 648 | Extract air damper type | 0:None, 1:OnOff, 2:3P, 3:OpenClose, 4: Spring-return | 0 | Service | 2018-03-28
HR_SERVICE_EXTRACT_DAMPER_OPEN_TIME | 649 | Extract air damper open time | 0..255 (seconds) | 60 | Service | 2018-03-28
HR_SERVICE_FILTERS_PRESS_RELE_TYPE | 650 | Filters pressure relay type | 0:None, 1:Supply, 2:Extract, 3.Both | 0 | Service | 2015-12-16
HR_SERVICE_CONTROL_BOX_HEATING_TEMPERATURE_SET_POINT | 651 | Controller cabinet temperature Set Point | 1..30 °C | 10 | Service | 2015-12-08
HR_SERVICE_AIR_QUALITY_SENSOR_1 | 652 | Supply air 1 quality sensor | 0:None, 1:Supply RH, 3:Extract RH, 4:Extract CO2, 5: Supply pressure, 6: Supply pressure 2 | 0 | Service | 2018-03-28
HR_SERVICE_AIR_QUALITY_SENSOR_1_MIN | 653 | Supply air 1 quality sensor MIN | 0..3000 ppm/0..1000*0.1%/0..3000Pa/0..3000Pa | 0 | Service | 2018-03-28
HR_SERVICE_AIR_QUALITY_SENSOR_1_MAX | 654 | Supply air 1 quality sensor MAX | 0..3000 ppm/0..1000*0.1%/0..3000Pa/0..3000Pa | 2000 | Service | 2018-03-28
HR_SERVICE_AIR_QUALITY_SENSOR_2 | 655 | Extract air 2 quality sensor | 0:None, 1:Supply RH, 3:Extract RH, 4:Extract CO2, 5: Extract pressure, 6: Extract pressure 2 | 0 | Service | 2018-03-28
HR_SERVICE_AIR_QUALITY_SENSOR_2_MIN | 656 | Extract air 2 quality sensor MIN | 0..3000 ppm/0..1000*0.1%/0..3000Pa/0..3000Pa | 0 | Service | 2018-03-28
HR_SERVICE_AIR_QUALITY_SENSOR_2_MAX | 657 | Extract air 2 quality sensor MAX | 0..3000 ppm/0..1000*0.1%/0..3000Pa/0..3000Pa | 2000 | Service | 2018-03-28
HR_SERVICE_DX_COOLER_TYPE | 658 | DX cooler type | 0:None, 1:0-10V, 2:On/Off | 0 | Service | 2016-05-05
HR_AUTO_ALARM_RESET_TIME | 659 | Auto alarm reseting time | 0: Not active, 1 - 24 h | 3 | Service | 2016-05-05
HR_SERVICE_FILTERS_TIMER_LIMIT | 660 | Filters timer limit | 1 - 365 (days) | 90 | Service | 2015-11-26
HR_SERVICE_SUPPLY_TEMPERATURE_LOW_LIMIT | 661 | Supply temperature LOW limit | 0 - 200 *0,1 °C | 165 | Service | 2015-07-10
HR_SERVICE_SUPPLY_TEMPERATURE_HIGH_LIMIT | 662 | Supply temperature HIGH limit | 200 - 600*0,1 °C | 400 | Service | 2015-07-10
HR_SERVICE_SUPPLY_TEMPERATURE_LIMIT_TIMEOUT | 663 | Supply temperature limit timeout | 0 - 1000 (seconds) | 500 | Service | 2015-07-10
HR_SERVICE_SUPPLY_TEMPERATURE_LIMIT_ALARM_ACTION | 664 | Supply temperature limit alarm action | 0: None, 1:Show warning, 2: Stop system | 1 | Service | 2017-02-13
HR_SERVICE_WATER_TEMPERATURE_LOW_LIMIT | 665 | Water temperature LOW limit | (-30)..10°C | 5 | Service | 2015-07-10
HR_SERVICE_HYDRONIC_PUMP_EXERCISE_INTERVAL | 666 | Hydronic pump Exercise interval | 1-30 (days) | 10 | Service | 2015-12-08
HR_SERVICE_STANDBY_BLOCKING_MODE | 667 | Standby blocking mode | 0:Never, 1:Always, 2:In Winter, 3:In Summer | 2 | Service | 2015-12-10
HR_SERVICE_STANDBY_BLOCKING_STANDBY_TIME_LIMIT_PER_DAY | 668 | Standby blocking: standby time limit per day | 0 - 500 (minutes) | 60 | Service | 2015-07-10
Reserved
HR_SERVICE_TEMPERATURE_CONTROL_TYPE | 670 | Temperature control type | 0: Supply, 1:Extract (room) | 0 | Service | 2015-07-10
HR_SERVICE_SUPPLY_TEMPERATURE_COMPENSATION | 671 | Supply temperature compensation | 0..100% | 50 | Service | 2015-07-10
HR_SERVICE_Comunication_1_ADDRESS | 672 | Comunication 1 Address | 1..247 | 1 | Service | 2015-07-10
HR_SERVICE_Comunication_1_BAUDRATE | 673 | Comunication 1 Baudrate | 0:1200, 1:2400, 2:4800, 3:9600, 4:19200, 5:38400, 6:57600, 7:115200 | 4 | Service | 2015-07-10
HR_SERVICE_Comunication_1_SETTINGS | 674 | Comunication 1 Frame settings | 0:N,8,1; 1:E,8,1; 2:O,8,1; 3:N,8,2; 4:E,8,2; 5:O,8,2; | 1 | Service | 2015-07-10
HR_SERVICE_Comunication_2_ADDRESS | 675 | Comunication 2 Address | 1..247 | 1 | Service | 2015-07-10
HR_SERVICE_Comunication_2_BAUDRATE | 676 | Comunication 2 Baudrate | 0:1200, 1:2400, 2:4800, 3:9600, 4:19200, 5:38400, 6:57600, 7:115200 | 4 | Service | 2015-07-10
HR_SERVICE_Comunication_2_SETTINGS | 677 | Comunication 2 Frame settings | 0:N,8,1; 1:E,8,1; 2:O,8,1; 3:N,8,2; 4:E,8,2; 5:O,8,2; | 1 | Service | 2015-07-10
HR_SERVICE_ROTOR_OUTPUT_TYPE | 678 | Rotor type | 0: 10V, 1: on/off | 0 | Service | 2015-07-10
HR_SERVICE_CO2_SETPOINT | 679 | CO2 Set Point | 0-3000 (ppm) | 700 | User | 2017-12-04
HR_SERVICE_CO2_CRITICAL_DIFF | 680 | CO2 allowed difference from Set Point | 0-3000 (ppm) | 200 | Service | 2017-12-04
HR_SERVICE_FANS_PRESSURE_PROTECTION_TIME | 681 | Pressure Protection time | 0-1000 (seconds) | 60 | Service | 2015-07-10
HR_SERVICE_K_FACTOR_EXTRACT | 682 | Extract K factor | 0..10000*0.1 | 0 | Service | 2015-07-10
HR_SERVICE_DX_COOLER_DEFROST_TIME | 683 | DX cooler min. defrost time | 30 - 600 | 60 | Service | 2016-05-05
HR_SERVICE_CRITICAL_TEMP | 684 | Critial outside air temperature | (-500..0)*0,1 °C | -150 | Service | 2016-05-05
HR_SERVICE_BYPASS_LIMIT | 685 | Byppass opening/closing limit | 0..1000*0.1(%) | 100 | Service | 2015-07-10
HR_SERVICE_ANTIFROST_EXHAUST_SET | 686 | Use exhaust frost temperature | 0:Not Active, 1 ..200*0,1 °C | 0 | Service | 2015-10-27
HR_SERVICE_ANTIFROST_EXHAUST_DIFF | 687 | Use frost temperature and exhaust tempearute difference | 0:Not Active, 1 .. 100*0,1 °C | 0 | Service | 2015-10-27
HR_SERVICE_ANTIFROST_PRESSURE | 688 | Use Heat exhanger pressure relay | 0:Not Active, 1:Active | 0 | Service | 2016-10-12
HR_SERVICE_ANTIFROST_PREHEATER | 689 | Use pre-heater for antifrost | 0:Not Active, 1:Active | 1 | Service | 2015-10-27
HR_SERVICE_ANTIFROST_RECIRCULATION | 690 | Use recirculation for antifrost | 0:Not Active, 1:Active | 0 | Service | 2015-10-27
HR_SERVICE_ANTIFROST_FAN | 691 | Use fan's for antifrost | 0:Not Active, 1:Disbalance, 2:Slow down by exhaust temperature | 0 | Service | 2018-08-21
HR_SERVICE_ANTIFROST_BYPASS_ROTOR | 692 | Use bypass/rotor for antifrost | 0:Not Active, 1:Active | 0 | Service | 2015-10-27
HR_SERVICE_ANTIFROST_CHANGE_TIME | 693 | Antifrost protection changing time | 1-600 (minutes) | 30 | Service | 2015-10-27
HR_SERVICE_HEAT_EXCHANGER_DAMPER_TYPE | 694 | Heat exchanger damper type | 1:One damper, 2: 2 segments, 3: 3 segments, 4:Remote controller | 1 | Service | 2016-08-30
HR_SERVICE_RESERVED_AI_VDC_TYPE | 695 | Reserverd VDC AI type | 0:None, 1:Heat exchanger pressure, 2: DX coil pressure | 0 | Service | 2017-09-18
HR_SERVICE_RESERVED_AI_VDC_MIN | 696 | Reserverd VDC AI MIN | 0..3000Pa | 0 | Service | 2016-08-30
HR_SERVICE_RESERVED_AI_VDC_MAX | 697 | Reserverd VDC AI MAX | 0..3000Pa | 1000 | Service | 2016-08-30
HR_SERVICE_AIR_QUALITY_SENSOR_1_VOLTAGE | 698 | Air quality sensor 1 input voltage range | 0:0-10V, 1:1-10V, 2:0-5V, 3:0.6-2.7V, 4:0-3.3V | 0 | Service | 2016-08-30
HR_SERVICE_AIR_QUALITY_SENSOR_2_VOLTAGE | 699 | Air quality sensor 2 input voltage range | 0:0-10V, 1:1-10V, 2:0-5V, 3:0.6-2.7V, 4:0-3.3V | 0 | Service | 2016-08-30
HR_SERVICE_RESERVED_AI_VDC_VOLTAGE | 700 | Reserverd VDC AI voltage range | 0:0-10V, 1:1-10V, 2:0-5V, 3:0.6-2.7V, 4:0-3.3V | 0 | Service | 2016-08-30
HR_SERVICE_HCOOLER_TYPE | 701 | Hydronic cooler type | 0:None, 1:Cooler, 2:Cooler/Heater | 0 | Service | 2016-08-30
HR_SERVICE_HCOOLER_CHANGEOVER_TYPE | 702 | Hydronic cooler changeover type | 0:By heating season, 1:By liquid temperature, 2:By digital input | 0 | Service | 2017-06-16
HR_SERVICE_DX_COOLER_MIN_TEMP | 703 | Min. outdoor air temperature for DX cooler | -500..200*0,1 °C | -200 | Service | 2017-04-27
HR_SERVICE_SUPPLY_FILTER_OVERPRESSURE | 704 | Supply air filter allowed overpressure | 0..100% | 30 | Service | 2017-09-27
HR_SERVICE_SUPPLY_FILTER_PRESSURE_LIMIT_1 | 705 | Supply air filter allowed overpressure limit 1 | 0..1000Pa | 150 | Service | 2017-11-29
HR_SERVICE_SUPPLY_FILTER_PRESSURE_LIMIT_2 | 706 | Supply air filter allowed overpressure limit 2 | 0..1000Pa | 200 | Service | 2017-11-29
HR_SERVICE_SUPPLY_FILTER_PRESSURE_LIMIT_3 | 707 | Supply air filter allowed overpressure limit 3 | 0..1000Pa | 250 | Service | 2017-11-29
HR_SERVICE_SUPPLY_FILTER_PRESSURE_LIMIT_4 | 708 | Supply air filter allowed overpressure limit 4 | 0..1000Pa | 300 | Service | 2017-11-29
HR_SERVICE_EXTRACT_FILTER_OVERPRESSURE | 709 | Extract air filter allowed overpressure | 0..100% | 30 | Service | 2017-09-27
HR_SERVICE_EXTRACT_FILTER_PRESSURE_LIMIT_1 | 710 | Extract air filter allowed overpressure limit 1 | 0..1000Pa | 150 | Service | 2017-11-29
HR_SERVICE_EXTRACT_FILTER_PRESSURE_LIMIT_2 | 711 | Extract air filter allowed overpressure limit 2 | 0..1000Pa | 200 | Service | 2017-11-29
HR_SERVICE_EXTRACT_FILTER_PRESSURE_LIMIT_3 | 712 | Extract air filter allowed overpressure limit 3 | 0..1000Pa | 250 | Service | 2017-11-29
HR_SERVICE_EXTRACT_FILTER_PRESSURE_LIMIT_4 | 713 | Extract air filter allowed overpressure limit 4 | 0..1000Pa | 300 | Service | 2017-11-29
HR_SERVICE_HEAT_EXCHANGER_OVERPRESSURE | 714 | Heat exchanger allowed overpressure | 0..100% | 30 | Service | 2017-09-27
HR_SERVICE_HEAT_EXCHANGER_PRESSURE_LIMIT_1 | 715 | Heat exchanger allowed overpressure limit 1 | 0..1000Pa | 150 | Service | 2017-11-29
HR_SERVICE_HEAT_EXCHANGER_PRESSURE_LIMIT_2 | 716 | Heat exchanger allowed overpressure limit 2 | 0..1000Pa | 200 | Service | 2017-11-29
HR_SERVICE_HEAT_EXCHANGER_PRESSURE_LIMIT_3 | 717 | Heat exchanger allowed overpressure limit 3 | 0..1000Pa | 250 | Service | 2017-11-29
HR_SERVICE_HEAT_EXCHANGER_PRESSURE_LIMIT_4 | 718 | Heat exchanger allowed overpressure limit 4 | 0..1000Pa | 300 | Service | 2017-11-29
HR_SERVICE_DX_COIL_OVERPRESSURE | 719 | DX cooler coil allowed overpressure | 0..100% | 30 | Service | 2017-09-27
HR_SERVICE_DX_COIL_PRESSURE_LIMIT_1 | 720 | DX cooler coil allowed overpressure limit 1 | 0..1000Pa | 150 | Service | 2017-11-29
HR_SERVICE_DX_COIL_PRESSURE_LIMIT_2 | 721 | DX cooler coil allowed overpressure limit 2 | 0..1000Pa | 200 | Service | 2017-11-29
HR_SERVICE_DX_COIL_PRESSURE_LIMIT_3 | 722 | DX cooler coil allowed overpressure limit 3 | 0..1000Pa | 250 | Service | 2017-11-29
HR_SERVICE_DX_COIL_PRESSURE_LIMIT_4 | 723 | DX cooler coil allowed overpressure limit 4 | 0..1000Pa | 300 | Service | 2017-11-29
HR_SERVICE_MAX_FAN_SPEED_CHANGE_RATIO_DX_ACTIVE | 724 | Fan speed max change per second when DX cooler is active | 0..1000*0,1% | 10 | Service | 2017-09-18
HR_SERVICE_NOMINAL_SUPPLY_AIR_FLOW | 725 | Nominal supply air flow | 0..30000 m3/h | 0 | Service | 2017-09-18
HR_SERVICE_NOMINAL_EXTRACT_AIR_FLOW | 726 | Nominal extract air flow | 0..30000 m3/h | 0 | Service | 2017-09-18
HR_SERVICE_MINIMAL_SUPPLY_AIR_FLOW | 727 | Minimal supply air flow for DX cooler | 0..30000 m3/h | 0 | Service | 2017-09-18
HR_SERVICE_DX_COOLER_DEFROST_INTERVAL | 728 | DX cooler defrost interval | 0..360 min. | 20 | Service | 2018-03-01
HR_SERVICE_DX_COOLER_OPTIMAL_DEFROST_TIME | 729 | DX cooler optimal defrost time | 0..3600 s | 180 | Service | 2018-03-01
HR_SERVICE_SUPPLY_DAMPER_TYPE | 730 | Supply air damper type | 0:None, 1:OnOff, 2:3P, 3:OpenClose, 4: Spring-return | 0 | Service | 2018-03-28
HR_SERVICE_SUPPLY_DAMPER_OPEN_TIME | 731 | Supply air damper open time | 0..255 (seconds) | 60 | Service | 2018-03-28
HR_SERVICE_FIRE_PROTECTION_INPUT_BOOT_TIME | 732 | Fire protection booting time | 0..300 (seconds) | 120 | Service | 2018-05-02
HR_SERVICE_FIRE_PROTECTION2_ACTION | 733 | Fire protection mode | 0: Stop system, 1:Supply air, 2:Extract air, 3:Both | 0 | Service | 2018-05-02
HR_SERVICE_FIRE_PROTECTION2_INPUT_TIMEOUT | 734 | Fire protection input timeout | 0..100 (seconds) | 10 | Service | 2018-05-02
HR_SERVICE_FIRE_PROTECTION2_INPUT_BOOT_TIME | 735 | Fire protection 2 booting time | 0..300 (seconds) | 120 | Service | 2018-05-02
HR_SERVICE_END_SW_INPUT_TIMEOUT | 736 | Fire damper end switch timeout | 0..600 (seconds) | 10 | Service | 2018-09-21
HR_SERVICE_SETPOINT_INTEGRATION_BY_EXTRACT_T | 737 | Supply temperature setpoint by extract temperature integration coeficient | 0..1000*0.1% | 0 | Service | 2018-09-21
HR_SERVICE_HYDRONIC_HEATER_REQUIRED_RETURN_WATER_TEMPERATURE | 738 | Hydronic heater required return water temperature | (-10..30) °C | 20 | Service | 2018-12-19
HR_SERVICE_HYDRONIC_PREHEATER_REQUIRED_RETURN_WATER_TEMPERATURE | 739 | Hydronic pre-heater required return water temperature | (-10..30) °C | 20 | Service | 2018-12-19
HR_SERVICE_SUPPLY_AIR_FLOW_LIMIT_1 | 740 | Supply air flow limit 1 | 0..30000 m3/h | 0 | Service | 2018-12-19
HR_SERVICE_EXTRACT_AIR_FLOW_LIMIT_1 | 741 | Extract air flow limit 1 | 0..30000 m3/h | 0 | Service | 2018-12-19
HR_SERVICE_SUPPLY_AIR_FLOW_LIMIT_2 | 742 | Supply air flow limit 2 | 0..30000 m3/h | 0 | Service | 2018-12-19
HR_SERVICE_EXTRACT_AIR_FLOW_LIMIT_2 | 743 | Extract air flow limit 2 | 0..30000 m3/h | 0 | Service | 2018-12-19
HR_SERVICE_SUPPLY_AIR_FLOW_LIMIT_3 | 744 | Supply air flow limit 3 | 0..30000 m3/h | 0 | Service | 2018-12-19
HR_SERVICE_EXTRACT_AIR_FLOW_LIMIT_3 | 745 | Extract air flow limit 3 | 0..30000 m3/h | 0 | Service | 2018-12-19
HR_SERVICE_SUPPLY_AIR_FLOW_LIMIT_4 | 746 | Supply air flow limit 4 | 0..30000 m3/h | 0 | Service | 2018-12-19
HR_SERVICE_EXTRACT_AIR_FLOW_LIMIT_4 | 747 | Extract air flow limit 4 | 0..30000 m3/h | 0 | Service | 2018-12-19
HR_SERVICE_CRITICAL_HX_OVERPRESSURE | 748 | Critical Heat exchanger overpressure | 0..200 Pa | 70 | Service | 2018-12-19
HR_SERVICE_HYDRONIC_HEATER_FROST_PROTECTION_SPEEDUP | 749 | Hydronic heater frost protection speedup | 0…1000*0.1% | 50 | Service | 2019-03-14
HR_SERVICE_HYDRONIC_PREHEATER_FROST_PROTECTION_SPEEDUP | 750 | Hydronic pre-heater frost protection speedup | 0…1000*0.1% | 50 | Service | 2019-03-14
HR_SERVICE_HYDRONIC_HEATER_MIN_VALVE_IN_WINTER | 751 | Hydronic heater min valve value in winter mode | 0…1000*0.1% | 50 | Service | 2019-03-14
HR_SERVICE_HYDRONIC_PREHEATER_MIN_VALVE_IN_WINTER | 752 | Hydronic pre-heater min valve value in winter mode | 0…1000*0.1% | 50 | Service | 2019-03-14
HR_SERVICE_AFTER_HX_TEMPERATURE_SENSOR_TYPE | 753 | After heat exchanger temperature sensor type | 0:None,1:Remote, 2:NTC 10K 3997, 2750...5000 (Custom NTC beta) | 0 | Service | 2019-03-14
HR_SERVICE_AFTER_HX_TEMPERATURE_SENSOR_ALARM_ACTION | 754 | After heat exchanger temperature sensor alarm action | 0: None, 1:Stop system, 2:Emergency run | 1 | Service | 2019-03-14
HR_SERVICE_HYDRONIC_HEATER_PID_PAUSE_SEC | 755 | Hydronic heater PID pause | 0…180 sec | 60 | Service | 2019-03-14
HR_SERVICE_HYDRONIC_HEATER_PID_PAUSE_THRESHOLD | 756 | Hydronic heater PID pause threshold | 0…50*0.1 °C | 5 | Service | 2019-03-14
HR_SERVICE_HYDRONIC_PREHEATER_PID_PAUSE_SEC | 757 | Hydronic pre-heater PID pause | 0…180 (seconds) | 60 | Service | 2019-03-14
HR_SERVICE_HYDRONIC_PREHEATER_PID_PAUSE_THRESHOLD | 758 | Hydronic pre-heater PID pause threshold | 0…50*0.1 °C | 5 | Service | 2019-03-14
HR_SERVICE_TEMP_CONTROLLER_PID_PAUSE_SEC | 759 | Temperature controller PID pause | 0…180 (seconds) | 60 | Service | 2019-03-14
HR_SERVICE_TEMP_CONTROLLER_PID_PAUSE_THRESHOLD | 760 | Temperature controller PID pause threshold | 0…50*0.1 °C | 5 | Service | 2019-03-14
HR_SERVICE_EL_PREHEATER_SET_POINT | 761 | Electrical pre-heater set point | (-1):Auto, (-300…100)*0.1°C | -1 | Service | 2019-03-14
HR_SERVICE_AHU_MODE_COOKERHOOD_ON | 762 | AHU mode then CookerHood on | 0…4 | 4 | Service | 2026-04-22
HR_SERVICE_COOKERHOOD_TIMER1 | 763 | CookerHood Timer 1 | 0…300 | 30 | Service | 2026-04-22
HR_SERVICE_COOKERHOOD_TIMER2 | 764 | CookerHood Timer 2 | 0…300 | 60 | Service | 2026-04-22
HR_SERVICE_COOKERHOOD_TIMER3 | 765 | CookerHood Timer 3 | 0…300 | 90 | Service | 2026-04-22
|  | Reserved |  |  | Service
Remote sensors input
DEFINE | Address | Name | Values | Default | User level | Updated
HR_REMOTE_SUPPLY_AIR_TEMPERATURE_SENSOR_REMOTE_VALUE | 800 | Supply air temperature sensor remote value | (-500..1000)*0,1 °C | 0 | - | 2015-07-10
HR_REMOTE_EXTRACT_AIR_TEMPERATURE_SENSOR_REMOTE_VALUE | 801 | Extract air temperature sensor remote value | (-500..1000)*0,1 °C | 0 | - | 2015-07-10
HR_REMOTE_EXHAUST_AIR_TEMPERATURE_SENSOR_REMOTE_VALUE | 802 | Exhaust air temperature sensor remote value | (-500..1000)*0,1 °C | 0 | - | 2015-07-10
HR_REMOTE_OUTDOOR_AIR_TEMPERATURE_SENSOR_REMOTE_VALUE | 803 | Outdoor air temperature sensor remote value | (-500..1000)*0,1 °C | 0 | - | 2017-04-27
HR_REMOTE_HYDRONIC_HEATER_WATER_SENSOR_REMOTE_VALUE | 804 | Hydronic heater water temperature sensor remote value | (-500..1000)*0,1 °C | 0 | - | 2015-12-08
HR_REMOTE_HYDRONIC_PREHEATER_WATER_SENSOR_REMOTE_VALUE | 805 | Hydronic pre-heater water temperature sensor remote value | (-500..1000)*0,1 °C | 0 | - | 2015-12-08
HR_REMOTE_HYDRONIC_COOLER_WATER_SENSOR_REMOTE_VALUE | 806 | Hydronic cooler water temperature sensor remote value | (-500..1000)*0,1 °C | 0 | - | 2015-12-08
HR_REMOTE_CONTROL_BOX_TEMPERATURE_SENSOR_REMOTE_VALUE | 807 | Controller cabinet temperature sensor remote value | (-500..1000)*0,1 °C | 0 | - | 2015-12-08
HR_REMOTE_EXTRACT_RH | 808 | Extract air humidity sensor remote value | 0..100% | 0 | - | 2016-05-05
HR_REMOTE_SUPPLY_RH | 809 | Supply air humidity sensor remote value | 0..100% | 0 | - | 2016-05-05
HR_REMOTE_EXTRACT_CO2 | 810 | Extract air CO2 sensor remote value | 0..2000ppm | 0 | - | 2016-05-05
HR_REMOTE_SUPPLY_CO2 | 811 | Supply air CO2 sensor remote value | 0..2000ppm | 0 | - | 2015-12-08
HR_REMOTE_SUPPLY_PRESSURE | 812 | Supply air pressure | 0..20000Pa | 0 | - | 2016-08-30
HR_REMOTE_EXTRACT_PRESSURE | 813 | Extract air pressure | 0..20000Pa | 0 | - | 2016-08-30
HR_REMOTE_DX_COOLER_RUN | 814 | DX cooler run | 0..100% | 0 | - | 2016-08-30
HR_REMOTE_DX_COOLER_DEFROST | 815 | DX cooler defrost stage | 0..9 | 0 | - | 2016-08-30
HR_REMOTE_SUPPLY_FILTER_PRESSURE | 816 | Supply filter pressure | 0..30000Pa | 0 | - | 2017-04-27
HR_REMOTE_EXTRACT_FILTER_PRESSURE | 817 | Extract filter pressure | 0..30000Pa | 0 | - | 2017-04-27
HR_REMOTE_HEAT_EXCHANGER_PRESSURE | 818 | Heat exchanger pressure | 0..30000Pa | 0 | - | 2017-04-27
HR_REMOTE_DX_COIL_PRESSURE | 819 | DX cooler coil pressure | 0..30000Pa | 0 | - | 2017-04-27
HR_REMOTE_HW_SYSTEM_MODE | 820 | Honey well system mode | 0..4 | 0 | - | 2017-09-18
HR_REMOTE_SUPPLY_AIR_FLOW_DIFF_PRESSURE | 821 | Supply air flow pressure 2 | 0..30000Pa | 0 | - | 2017-09-18
HR_REMOTE_EXTRACT_AIR_FLOW_DIFF_PRESSURE | 822 | Extract air flow pressure 2 | 0..30000Pa | 0 | - | 2017-09-18
HR_REMOTE_DX_COOLER_DEFROST_2 | 823 | DX cooler defrost stage (circuit 2) | 0..9 | 0 | - | 2017-11-29
HR_REMOTE_DX_COOLER_DEFROST_3 | 824 | DX cooler defrost stage (circuit 3) | 0..9 | 0 | - | 2017-11-29
HR_REMOTE_CONTROLLER_HEATING_POWER | 825 | Remote expansion controller heating power | 0..1000 | 0 | - | 2018-05-02
HR_REMOTE_CONTROLLER_PRE_HEATING_POWER | 826 | Remote expansion controller pre-heating power | 0..1000 | 0 | - | 2018-05-02
HR_REMOTE_CONTROLLER_COOLING_POWER | 827 | Remote expansion controller cooling power | 0..1000 | 0 | - | 2018-05-02
HR_REMOTE_AFTER_HX_TEMPERATURE_SENSOR_REMOTE_VALUE | 828 | After heat exchanger temperature sensor remote value | (-500..1000)*0,1 °C | 0 | - | 2019-03-14
Reserved
Manufacture functions
DEFINE | Address | Name | Values | Default | User level | Updated
HR_MANUFACTURE_CLEAR_MEMORY | 850 | Clear memory | Code 220 | 0 |  | 2015-07-10
HR_MANUFACTURE_TEMPERATURE_SENSORS_CALIBRATION | 851 | Temperature sensors calibration | 0:No 1-3:Step of current calibration | 0 |  | 2015-07-15
HR_MANUFACTURE_BACKUP_CONFIGURATION | 852 | Backup configuration | Code 220 | 0 |  | 2015-07-10
HR_MANUFACTURE_SELF_CALIBRATION | 853 | Self calibration (Bypass, Pressure..) | 0:None;Bypass stepper: 200; Recirculation stepper: 210; Pressure: 220; | 0 |  | 2015-07-10
HR_MANUFACTURE_PUK_CODE_1 | 854 | PUK code 1 | Code 222 | 0 |  | 2015-07-10
HR_MANUFACTURE_PUK_CODE_2 | 855 | PUK code 2 | Code 202 | 0 |  | 2015-07-10
HR_MANUFACTURE_PUK_CODE_3 | 856 | PUK code 3 | Code 220 | 0 |  | 2015-07-10
HR_MANUFACTURE_CONFIGURATION_VERSION | 857 | Config Version | 100-999 | 0 |  | 2016-01-05
HR_MANUFACTURE_TEST_MODE | 858 | Testing mode | 0: Normal operation 1-255:Test step | 0 |  | 2015-07-15
HR_MANUFACTURE_AHU_ID_1 | 859 | Set AHU ID 1 | 0 - 9999 | 0 |  | 2015-10-27
HR_MANUFACTURE_AHU_ID_2 | 860 | Set AHU ID 2 | 0 - 9999 | 0 |  | 2015-10-27
HR_MANUFACTURE_AHU_ID_3 | 861 | Set AHU ID 3 | 0 - 9999 | 0 |  | 2015-10-27
HR_MANUFACTURE_AHU_ID_4 | 862 | Set AHU ID 4 | 0 - 9999 | 0 |  | 2015-10-27
HR_MANUFACTURE_AHU_ID_5 | 863 | Set AHU ID 5 | 0 - 9999 | 0 |  | 2015-10-27
I/O map functions
DEFINE | Address | Name | Values | Default | User level | Updated
HR_IO_MAP_MCB_DI1 | 900 | MCB DI1 function | DI | 13 |  | 2017-09-18
HR_IO_MAP_MCB_DI2 | 901 | MCB DI2 function | DI | 12 |  | 2017-09-18
HR_IO_MAP_MCB_DI3 | 902 | MCB DI3 function | DI | 3 |  | 2017-09-18
HR_IO_MAP_MCB_DI4 | 903 | MCB DI4 function | DI | 20 |  | 2017-09-18
HR_IO_MAP_MCB_DI5 | 904 | MCB DI5 function | DI | 7 |  | 2017-09-18
HR_IO_MAP_MCB_DI6 | 905 | MCB DI6 function | DI | 8 |  | 2017-09-18
HR_IO_MAP_MCB_DI7 | 906 | MCB DI7 function | DI | 5 |  | 2017-09-18
HR_IO_MAP_MCB_DI8 | 907 | MCB DI8 function | DI | 9 |  | 2017-09-18
HR_IO_MAP_MCB_DI9 | 908 | MCB DI9 function | DI | 6 |  | 2017-09-18
HR_IO_MAP_MCB_DI10 | 909 | MCB DI10 function | DI | 4 |  | 2017-09-18
HR_IO_MAP_MCB_AI1_NTC | 910 | MCB AI1 NTC function | NTC | 1 |  | 2017-09-18
HR_IO_MAP_MCB_AI2_NTC | 911 | MCB AI2 NTC function | NTC | 2 |  | 2017-09-18
HR_IO_MAP_MCB_AI3_NTC | 912 | MCB AI3 NTC function | NTC | 3 |  | 2017-09-18
HR_IO_MAP_MCB_AI4_VDC | 913 | MCB AI4 VDC function | VDC | 3 |  | 2017-09-18
HR_IO_MAP_MCB_AI5_NTC | 914 | MCB AI5 NTC function | NTC | 4 |  | 2017-09-18
HR_IO_MAP_MCB_AI6_NTC | 915 | MCB AI6 NTC function | NTC | 9 |  | 2017-09-18
HR_IO_MAP_MCB_AI7_NTC | 916 | MCB AI7 NTC function | NTC | 5 |  | 2017-09-18
HR_IO_MAP_MCB_DO2 | 917 | MCB DO2 function | DO | 3 |  | 2017-09-18
HR_IO_MAP_MCB_DO3 | 918 | MCB DO3 function | DO | 4 |  | 2017-09-18
HR_IO_MAP_MCB_DO4 | 919 | MCB DO4 function | DO | 9 |  | 2017-09-18
HR_IO_MAP_MCB_DO5 | 920 | MCB DO5 function | DO | 10 |  | 2017-09-18
HR_IO_MAP_MCB_AO1 | 921 | MCB AO1 function | AO | 1 |  | 2017-09-18
HR_IO_MAP_MCB_AO2 | 922 | MCB AO2 function | AO | 2 |  | 2017-09-18
HR_IO_MAP_MCB_AO3 | 923 | MCB AO3 function | AO | 3 |  | 2017-09-18
HR_IO_MAP_EX1_DI1 | 924 | EX1 DI1 function | DI | 11 |  | 2017-09-18
HR_IO_MAP_EX1_DI2 | 925 | EX1 DI2 function | DI | 10 |  | 2017-09-18
HR_IO_MAP_EX1_DI3 | 926 | EX1 DI3 function | DI | 1 |  | 2017-09-18
HR_IO_MAP_EX1_DI4 | 927 | EX1 DI4 function | DI | 2 |  | 2017-09-18
HR_IO_MAP_EX1_DI5 | 928 | EX1 DI5 function | DI | 17 |  | 2017-09-18
HR_IO_MAP_EX1_DI6 | 929 | EX1 DI6 function | DI | 15 |  | 2017-09-18
HR_IO_MAP_EX1_DI7 | 930 | EX1 DI7 function | DI | 16 |  | 2017-09-18
HR_IO_MAP_EX1_DI8 | 931 | EX1 DI8 function | DI | 21 |  | 2017-09-18
HR_IO_MAP_EX1_DI9 | 932 | EX1 DI9 function | DI | 22 |  | 2017-09-18
HR_IO_MAP_EX1_DI10 | 933 | EX1 DI10 function | DI | 23 |  | 2017-09-18
HR_IO_MAP_EX1_DI11 | 934 | EX1 DI11 function | DI | 19 |  | 2017-09-18
HR_IO_MAP_EX1_AI1_VDC | 935 | EX1 AI1 VDC function | VDC | 1 |  | 2017-09-18
HR_IO_MAP_EX1_AI2_VDC | 936 | EX1 AI2 VDC function | VDC | 2 |  | 2017-09-18
HR_IO_MAP_EX1_AI3_VDC | 937 | EX1 AI3 VDC function | VDC | 0 |  | 2017-09-18
HR_IO_MAP_EX1_AI4_NTC | 938 | EX1 AI4 NTC function | NTC | 7 |  | 2017-09-18
HR_IO_MAP_EX1_AI5_NTC | 939 | EX1 AI5 NTC function | NTC | 6 |  | 2017-09-18
HR_IO_MAP_EX1_DO1 | 940 | EX1 DO1 function | DO | 20 |  | 2017-09-18
HR_IO_MAP_EX1_DO2 | 941 | EX1 DO2 function | DO | 21 |  | 2017-09-18
HR_IO_MAP_EX1_AO1 | 942 | EX1 AO1 function | AO | 4 |  | 2017-09-18
HR_IO_MAP_EX1_AO2 | 943 | EX1 AO2 function | AO | 5 |  | 2017-09-18
HR_IO_MAP_EX1_AO3 | 944 | EX1 AO3 function | AO | 6 |  | 2017-09-18
HR_IO_MAP_EX1_AO4 | 945 | EX1 AO4 function | AO | 7 |  | 2017-09-18
HR_IO_MAP_EX1_AO5 | 946 | EX1 AO5 function | AO | 8 |  | 2017-09-18
HR_IO_MAP_EX2_DO1 | 947 | EX2 DO1 function | DO | 13 |  | 2017-09-18
HR_IO_MAP_EX2_DO2 | 948 | EX2 DO2 function | DO | 13 |  | 2017-09-18
HR_IO_MAP_EX2_DO3 | 949 | EX2 DO3 function | DO | 14 |  | 2017-09-18
HR_IO_MAP_EX2_DO4 | 950 | EX2 DO4 function | DO | 15 |  | 2017-09-18
HR_IO_MAP_EX2_DO5 | 951 | EX2 DO5 function | DO | 11 |  | 2017-09-18
HR_IO_MAP_EX2_DO6 | 952 | EX2 DO6 function | DO | 12 |  | 2017-09-18
HR_IO_MAP_EX2_DO7 | 953 | EX2 DO7 function | DO | 5 |  | 2017-09-18
HR_IO_MAP_EX2_DO8 | 954 | EX2 DO8 function | DO | 16 |  | 2017-09-18
HR_IO_MAP_EX2_DO9 | 955 | EX2 DO9 function | DO | 18 |  | 2017-09-18
HR_IO_MAP_EX2_DO10 | 956 | EX2 DO10 function | DO | 19 |  | 2017-09-18
HR_IO_MAP_EX2_DO11 | 957 | EX2 DO11 function | DO | 17 |  | 2017-09-18
HR_IO_MAP_EX2_DO12 | 958 | EX2 DO12 function | DO | 2 |  | 2017-09-18
HR_IO_MAP_EX2_DO13 | 959 | EX2 DO13 function | DO | 2 |  | 2017-09-18
HR_IO_MAP_MINI_MCB_DI1 | 960 | MINI MCB DI1 function | DI | 9 |  | 2017-09-18
HR_IO_MAP_MINI_MCB_DI2 | 961 | MINI MCB DI2 function | DI | 4 |  | 2017-09-18
HR_IO_MAP_MINI_MCB_DI3 | 962 | MINI MCB DI3 function | DI | 6 |  | 2017-09-18
HR_IO_MAP_MINI_MCB_DI4 | 963 | MINI MCB DI4 function | DI | 20 |  | 2017-09-18
HR_IO_MAP_MINI_MCB_DI5 | 964 | MINI MCB DI5 function | DI | 13 |  | 2017-09-18
HR_IO_MAP_MINI_MCB_DI6 | 965 | MINI MCB DI6 function | DI | 12 |  | 2017-09-18
HR_IO_MAP_MINI_MCB_DI7 | 966 | MINI MCB DI7 function | DI | 7 |  | 2017-09-18
HR_IO_MAP_MINI_MCB_DI8 | 967 | MINI MCB DI8 function | DI | 8 |  | 2017-09-18
HR_IO_MAP_MINI_MCB_DI9 | 968 | MINI MCB DI9 function | DI | 1 |  | 2017-09-18
HR_IO_MAP_MINI_MCB_DI10 | 969 | MINI MCB DI10 function | DI | 2 |  | 2017-09-18
HR_IO_MAP_MINI_MCB_AI1_NTC | 970 | MINI MCB AI1 NTC function | NTC | 1 |  | 2017-09-18
HR_IO_MAP_MINI_MCB_AI2_NTC | 971 | MINI MCB AI2 NTC function | NTC | 2 |  | 2017-09-18
HR_IO_MAP_MINI_MCB_AI3_NTC | 972 | MINI MCB AI3 NTC function | NTC | 4 |  | 2017-09-18
HR_IO_MAP_MINI_MCB_AI4_NTC | 973 | MINI MCB AI4 NTC function | NTC | 3 |  | 2017-09-18
HR_IO_MAP_MINI_MCB_AI5_VDC | 974 | MINI MCB AI5 VDC function | VDC | 1 |  | 2017-09-18
HR_IO_MAP_MINI_MCB_DO1 | 975 | MINI MCB DO1 function | DO | 16 |  | 2017-09-18
HR_IO_MAP_MINI_MCB_DO2 | 976 | MINI MCB DO2 function | DO | 17 |  | 2017-09-18
HR_IO_MAP_MINI_MCB_DO3 | 977 | MINI MCB DO3 function | DO | 11 |  | 2017-09-18
HR_IO_MAP_MINI_MCB_DO4 | 978 | MINI MCB DO4 function | DO | 12 |  | 2017-09-18
HR_IO_MAP_MINI_MCB_DO5 | 979 | MINI MCB DO5 function | DO | 5 |  | 2017-09-18
HR_IO_MAP_MINI_MCB_DO6 | 980 | MINI MCB DO6 function | DO | 2 |  | 2017-09-18
HR_IO_MAP_MINI_MCB_AO1 | 981 | MINI MCB AO1 function | AO | 1 |  | 2017-09-18
HR_IO_MAP_MINI_MCB_AO2 | 982 | MINI MCB AO2 function | AO | 2 |  | 2017-09-18
HR_IO_MAP_MINI_MCB_AO3 | 983 | MINI MCB AO3 function | AO | 3 |  | 2017-09-18
HR_IO_MAP_MINI_EX1_DI1 | 984 | MINI EX1 DI1 function | DI | 10 |  | 2017-09-18
HR_IO_MAP_MINI_EX1_DI2 | 985 | MINI EX1 DI2 function | DI | 11 |  | 2017-09-18
HR_IO_MAP_MINI_EX1_DI3 | 986 | MINI EX1 DI3 function | DI | 15 |  | 2017-09-18
HR_IO_MAP_MINI_EX1_DI4 | 987 | MINI EX1 DI4 function | DI | 16 |  | 2017-09-18
HR_IO_MAP_MINI_EX1_AI1_VDC | 988 | MINI EX1 AI1 VDC function | VDC | 2 |  | 2017-09-18
HR_IO_MAP_MINI_EX1_AI2_NTC | 989 | MINI EX1 AI2 NTC function | NTC | 5 |  | 2017-09-18
HR_IO_MAP_MINI_EX1_DO1 | 990 | MINI EX1 DO1 function | DO | 20 |  | 2017-09-18
HR_IO_MAP_MINI_EX1_DO2 | 991 | MINI EX1 DO2 function | DO | 21 |  | 2017-09-18
HR_IO_MAP_MINI_EX1_AO1 | 992 | MINI EX1 AO1 function | AO | 4 |  | 2017-09-18
HR_IO_MAP_MCB_U3 | 993 | MCB U3 function | PS | 1 |  | 2017-09-18
HR_IO_MAP_MCB_U4 | 994 | MCB U4 function | PS | 2 |  | 2017-09-18
HR_IO_MAP_MINI_MCB_SK1 | 995 | MINI MCB SK1 function | PS | 1 |  | 2017-09-18
HR_IO_MAP_MINI_MCB_SK2 | 996 | MINI MCB SK2 function | PS | 2 |  | 2017-09-18
HR_IO_MAP_MCB_DO6 | 997 | MCB DO6 function | DO | 0 |  | 2019-06-07
HR_IO_MAP_MCB_DO7 | 998 | MCB DO7 function | DO | 0 |  | 2026-04-22
HR_IO_MAP_MCB_DO8 | 999 | MCB DO8 function | DO | 0 |  | 2026-04-22
HR_IO_MAP_MCB_DO9 | 1011 | MCB DO9 function | DO | 0 |  | 2026-04-22

## Coils
Coils, Read/Write
DEFINE | Address | Name | Value | Default | User level | Updated
COIL_FILTER_TIMER_RESET | 1 | Filters timer reset | 0: Nothing, 1:Activate | 0 | User | 2015-07-10
COIL_DATE_AND_TIME_SET_COMMAND | 2 | Date and time set: Set command | 0: Nothing, 1:Activate | 0 | User | 2015-07-10
COIL_DRYNESS_PROTECTION | 3 | Dryness protection | 0: Disabled, 1:Enabled | 0 | User | 2015-07-10
COIL_NIGHT_COOLING_FUNCTION | 4 | Night cooling function | 0: Disabled, 1:Enabled | 0 | User | 2015-07-10
COIL_INTENSIVE_AIR_FLOW_BOOST | 5 | Intensive air flow | 0: Nothing, 1:Activate | 0 | User | 2015-07-10
COIL_FULL_RECIRCULATION_ON_BUILDING_PROTECTION | 6 | Full recirculation on building protection mode | 0: Disabled, 1:Enabled | 0 | User | 2015-10-27
COIL_FULL_RECIRCULATION_ON_ECONOMY | 7 | Full recirculation on economy mode | 0: Disabled, 1:Enabled | 0 | User | 2015-10-27
COIL_AIR_FLOW_CONTROL_BY_RH | 8 | Air flow control by extract RH | 0: Disabled, 1:Enabled | 0 | User | 2016-08-30
COIL_POOL_FUNCTION | 9 | Pool function | 0: Disabled, 1:Enabled | 0 | User | 2017-11-29
Reserved
COIL_DO_FIRE_DAMPER_TEST | 50 | Do fire damper test | 0: Nothing, 1:Activate | 0 | Adjuster | 2015-07-10
COIL_SAVE_TO_EEPROM | 51 | Save to EEPROM | 0: Nothing, 1:Activate | 0 | Adjuster | 2015-07-10
COIL_SYSTEM_RESTART | 52 | System Restart | 0: Nothing, 1:Activate | 0 | Adjuster | 2015-07-10
COIL_GO_BACK | 53 | Go back to prevous mode | 0: Nothing, 1:Activate | 0 | Adjuster | 2015-10-30
COIL_CALIBRATE_PRESSURE_LIMITS | 54 | Calibrate pressure limits | 0: Nothing, 1:Activate | 0 | Service | 2017-04-27
COIL_REMOTE_HEATER_ALARM | 55 | Remote expansion heater alarm | 0: Nothing, 1:Activate | 0 | Service | 2018-05-02
COIL_REMOTE_HEATER_WARNING | 56 | Remote expansion heater warning | 0: Nothing, 1:Activate | 0 | Service | 2018-05-02
COIL_REMOTE_PRE_HEATER_ALARM | 57 | Remote expansion pre-heater alarm | 0: Nothing, 1:Activate | 0 | Service | 2018-05-02
COIL_REMOTE_PRE_HEATER_WARNING | 58 | Remote expansion pre-heater warning | 0: Nothing, 1:Activate | 0 | Service | 2018-05-02
COIL_REMOTE_COOLER_ALARM | 59 | Remote expansion cooler alarm | 0: Nothing, 1:Activate | 0 | Service | 2018-05-02
COIL_REMOTE_COOLER_WARNING | 60 | Remote expansion cooler warning | 0: Nothing, 1:Activate | 0 | Service | 2018-05-02
COIL_REMOTE_HEATER_COOLING_ON | 61 | Remote expansion heaters cooling ON | 0: Nothing, 1:Activate | 0 | Service | 2018-05-02
COIL_REMOTE_EL_HEATER_IS_ON | 62 | Remote expansion el. heater is ON | 0: Nothing, 1:Activate | 0 | Service | 2018-05-02
COIL_REMOTE_HYD_HEATER_INSTALLED | 63 | Remote expansion any hydronic heater installed | 0: Nothing, 1:Activate | 0 | Service | 2018-05-02
COIL_REMOTE_STOP_VENTILATION | 64 | Remote expansion stop ventilation | 0: Nothing, 1:Activate | 0 | Service | 2018-05-02
COIL_REMOTE_PREPARING | 65 | Remote expansion preparing | 0: Nothing, 1:Activate | 0 | Service | 2018-05-02
COIL_REMOTE_ALARM_RESET_OK | 66 | Remote expansion alarm reset | 0: Nothing, 1:Activate | 0 | Service | 2018-05-02
COIL_COOKERHOOD_DAMPER | 67 | CookerHood damper control | 0: Close, 1:Open | 0 | Service | 2026-04-22
COIL_COOKERHOOD_LIGHTING | 68 | CookerHood lighting control | 0: Off, 1:On | 0 | Service | 2026-04-22
Reserved
COIL_HEATER_MANUAL_PROTECTION | 100 | Heater manual protection | 0:NO, 1:NC | 0 | Service | 2015-07-10
COIL_HEATER_AUTOMATIC_PROTECTION | 101 | Heater automatic protection | 0:NO, 1:NC | 0 | Service | 2015-07-10
COIL_PREHEA_MANUAL_PROTECTION | 102 | Pre-heater manual protection | 0:NO, 1:NC | 0 | Service | 2015-07-10
COIL_PREHEA_AUTOMATIC_PROTECTION | 103 | Pre-heater automatic protection | 0:NO, 1:NC | 0 | Service | 2015-07-10
COIL_SUPPLY_FAN_PROTECTION | 104 | Supply fan protection | 0:NO, 1:NC | 0 | Service | 2015-07-10
COIL_EXTRAC_FAN_PROTECTION | 105 | Extract fan protection | 0:NO, 1:NC | 0 | Service | 2015-07-10
COIL_HX_PRESS_RELAY | 106 | Heat exchanger pressure relay | 0:NO, 1:NC | 0 | Service | 2015-11-09
COIL_BYPASS_CLOSED | 107 | Bypass closed | 0:NO, 1:NC | 0 | Service | 2015-07-10
COIL_DX_COOLER_PROTECTION | 108 | DX cooler protection | 0:NO, 1:NC | 0 | Service | 2015-07-10
COIL_REMOTE_MODE_SWITCH | 109 | Remote mode switch | 0:NO, 1:NC | 0 | Service | 2015-07-10
COIL_REMOTE_CUSTOM_FANS_SPEED_SWITCH | 110 | Remote custom fans speed switch | 0:NO, 1:NC | 0 | Service | 2015-07-10
COIL_FIRE_PROTECTION_INPUT | 111 | Fire protection input | 0:NO, 1:NC | 1 | Service | 2016-01-05
COIL_FIRE_DAMPER_OPENED | 112 | Fire damper opened | 0:NO, 1:NC | 0 | Service | 2015-07-10
COIL_FIRE_DAMPER_CLOSED | 113 | Fire damper closed | 0:NO, 1:NC | 0 | Service | 2015-07-10
COIL_SUPPLY_FILTER_PRESS_RELE | 114 | Supply filter press rele | 0:NO, 1:NC | 0 | Service | 2015-07-10
COIL_EXTRACT_FILTER_PRESS_RELE | 115 | Extract filter press rele | 0:NO, 1:NC | 0 | Service | 2015-07-10
COIL_FANS_PROTECTION_BY_RPM | 116 | Fans protection by RPM (Enable/Disable) | 0: Disabled, 1:Enabled | 0 | Service | 2015-07-10
COIL_FIXED_AIR_FLOWS | 117 | Fixed air flows | 0:No, 1:Yes | 1 | Service | 2015-07-10
COIL_T_SENSOR_BEFORE_PREHEATER | 118 | Outdoor air temp. sensor before pre-heater | 0:No, 1:Yes | 0 | Service | 2017-04-27
COIL_SLOW_DOWN_FANS_BY_TEMPERATURE | 119 | Slow down fans by temperature | 0: Disabled, 1:Enabled | 0 | Service | 2015-07-10
COIL_FIRE_DAMPER_TESTING | 120 | Fire damper testing | 0: Disabled, 1:Enabled | 0 | Service | 2015-07-10
COIL_FIRE_DAMPER_ACTION_ON_FIRE_ALARM | 121 | Fire damper action on fire alarm | 0: Open, 1:Close | 1 | Service | 2015-07-10
COIL_SUPPLY_RECIRCULATION_DAMPER | 122 | Supply recirculation damper | 0: Disabled, 1:Enabled | 0 | Service | 2017-11-29
COIL_CONTRO_BOX_HEATING | 123 | Controller cabinet temperature control | 0: Disabled, 1:Enabled | 0 | Service | 2015-11-26
COIL_FIRE_PLACE_PROTECTION | 124 | Fire place protection | 0: Disabled, 1:Enabled | 0 | Service | 2015-07-10
COIL_SERVIC_STOP_FUNCTION | 125 | Service stop function | 0: Disabled, 1:Enabled | 0 | Service | 2015-07-10
COIL_ROTOR_RPM_PROTECTION | 126 | Rotor RPM protection | 0: Disabled, 1:Enabled | 0 | Service | 2015-07-10
COIL_STOP_ON_ROTOR_FAULURE | 127 | Stop on rotor failure | 0: No, 1:Yes | 1 | Service | 2017-01-26
COIL_CO2_PROTECTION_ENABLED | 128 | CO2 Level monitoring (Disable/Enable) | 0: Disabled, 1:Enabled | 0 | Service | 2015-12-08
COIL_PRESSURE_PROTECTION_ENABLED | 129 | Fans pressure protection (Disable/Enable) | 0: Disabled, 1:Enabled | 0 | Service | 2015-11-26
COIL_FIRE_PLACE_PROTECTION_INPUT | 130 | Fire place protection input | 0:NO, 1:NC | 0 | Service | 2015-07-10
COIL_HEATER_PREHEATER | 131 | Heater/pre-heater control position | 0:Heater on basic, pre-heater on EX1; 1:Pre-heater on basic, jeater on EX1 | 0 | Service | 2015-10-27
COIL_RECIRCULATION_BY_TEMPERATURE | 132 | Recirculation by temperature | 0: Disabled, 1:Enabled | 0 | Service | 2015-11-09
COIL_CONTRO_BOX_FAN | 133 | Controller cabinet temperature controlled by | 0: Heater, 1:Fan | 0 | Service | 2015-12-08
COIL_SHOW_ALARMS_ON_COOKING_HOOD | 134 | Show alarms on cooking hood | 0: No, 1: Yes | 1 | Service | 2015-11-26
COIL_DX_COOLER_REVERSE_ENABLED | 135 | Enable DX cooler reverse | 0: Disabled, 1:Enabled | 0 | Service | 2016-01-07
COIL_DX_COOLER_DEFROST_INPUT | 136 | DX cooler defros input | 0:NO, 1:NC | 0 | Service | 2016-04-13
COIL_EX1_MODULE | 137 | EX1 module | 0: Disabled, 1:Enabled | 0 | Service | 2016-04-13
COIL_EX2_MODULE | 138 | EX2 module | 0: Disabled, 1:Enabled | 0 | Service | 2016-04-13
COIL_COMM_MODULE | 139 | Communication module | 0: Disabled, 1:Enabled | 0 | Service | 2016-04-13
COIL_HCOOLER_CHANGEOVER_INPUT | 140 | Hydronic cooler changeover input | 0:NO, 1:NC | 0 | Service | 2016-08-30
COIL_AIR_PRESSURE_FACTOR | 141 | Air pressure factor | 0:0.1, 1:1 | 0 | Service | 2017-04-27
COIL_TOO_HI_CONDENSATION_INPUT | 142 | Too high condensation level input | 0:NO, 1:NC | 0 | Service | 2017-04-27
COIL_SUPPLY_FAN_WARNING_INPUT | 143 | Supply fan warning input | 0:NO, 1:NC | 0 | Service | 2017-04-27
COIL_EXTRACT_FAN_WARNING_INPUT | 144 | Extract fan warning input | 0:NO, 1:NC | 0 | Service | 2017-04-27
COIL_EXTRACT_AIR_FLOW_BY_SUPLLY_AIR_FLOW | 145 | Enable extract air flow control by supply air flow | 0: Disabled, 1:Enabled | 0 | Service | 2017-09-18
COIL_EXTRACT_FAN_BY_SUPLLY_FAN | 146 | Enable extract air fan control by supply air fan | 0: Disabled, 1:Enabled | 0 | Service | 2017-09-28
COIL_OUTSIDE_RECIRCULATION_DAMPER | 147 | Outside recirculation damper | 0: Disabled, 1:Enabled | 0 | Service | 2017-11-29
COIL_DX_COOLER_DEFROST_AUTO_ADJUSTING | 148 | DX cooler defrost auto adjusting enable | 0: Disabled, 1:Enabled | 0 | Service | 2018-03-01
COIL_HEATER_CIRC_PUMP_PROTECTION_SYSTEM_STOP | 149 | Stop system on circ. pump failure | 0: Disabled, 1:Enabled | 0 | Service | 2018-03-01
COIL_HEATER_CIRC_PUMP_PROTECTION_INPUT | 150 | Heater circualtion pump protection input | 0:NO, 1:NC | 0 | Service | 2018-03-01
COIL_PRE_HEATER_CIRC_PUMP_PROTECTION_INPUT | 151 | Pre-heater circualtion pump protection input | 0:NO, 1:NC | 0 | Service | 2018-03-01
COIL_ENABLE_REMOTE_HEATING_COOLING_EXPANSION | 152 | Enable remote heaters/coolers expansion | 0: Disabled, 1:Enabled | 0 | Service | 2018-05-02
COIL_FIRE_PROTECTION2_INPUT | 153 | Fire protection 2 input | 0:NO, 1:NC | 0 | Service | 2018-05-02
COIL_HEAT_EXCHANGER_MAX_POWER_IN_WINTER | 154 | Use Heat exchanger max power in winter time | 0: Disabled, 1:Enabled | 0 | Service | 2018-12-19
COIL_SLAVE_FAN_EXTRACT_OR_SUPPLY | 155 | Select slave fan | 0: Extract, 1:Supply | 0 | Service | 2023-11-29
COIL_EL_HEATER_ON_OFF_USE_AO_OUTPUT | 156 | Use electrical heater AO output for Slow PWM | 0: Disabled, 1:Enabled | 0 | Service | 2026-04-22
COIL_COOKERHOOD | 157 | CookerHood installed | 0: Disabled, 1:Enabled | 0 | Service | 2026-04-22
Reserved
COIL_RESTOR_FACTORY_DEFAULTS | 200 | Restore factory settings | 0: Nothing, 1:Activate | 0 | Service | 2015-12-08
Reserved
COIL_CHANGE_PASSWORD | 202 | Change password | 0: Nothing, 1:Activate | 0 | Service | 2015-07-10

## Discrete inputs
Discrete inputs 0x02, Read only
Alarm list
DEFINE | Address | Name | Values | User level | Updated
ALARM_ROTOR_BROKEN_BELT_WARNING | 1 | Warning! Rotor broken belt alarm | 0:Not active, 1:Active | User | 2017-09-18
ALARM_FIREPLACE_PROTECTION_ACTIVATED | 2 | Alarm! Fireplace protection activated | 0:Not active, 1:Active | User | 2015-12-08
ALARM_DRYNESS_PROTECTION_ACTIVATED | 3 | Warning! Dryness protection activated | 0:Not active, 1:Active | User | 2015-12-08
ALARM_PLATE_HEAT_EXCHANGER_FROST_PROTECTION_ACTIVATED | 4 | Warning! Plate heat exchanger frost protection activated | 0:Not active, 1:Active | User | 2015-12-08
ALARM_PLATE_HEAT_EXCHANGER_FROST_PROTECTION_SYSTEM_STOPPED | 5 | Alarm! Plate heat exchanger frost protection system stopped | 0:Not active, 1:Active | User | 2015-12-08
ALARM_PLATE_HEAT_EXCHANGER_FROST_PROTECTION_PRESS_RELE | 6 | Warning! Plate heat exchanger frost protection (pressure relay) | 0:Not active, 1:Active | User | 2015-12-16
ALARM_HYDRONIC_HEATER_FROST_PROTECTION_SYSTEM_STOPPED | 7 | Alarm! Hydronic heater frost protection. System stopped. | 0:Not active, 1:Active | User | 2015-12-08
ALARM_TOO_LOW_SUPPLY_TEMPERATURE | 8 | Warning! Too low supply temperature | 0:Not active, 1:Active | User | 2015-12-08
ALARM_TOO_HIGH_SUPPLY_TEMPERATURE | 9 | Warning! Too high supply temperature | 0:Not active, 1:Active | User | 2015-12-08
ALARM_TOO_LOW_SUPPLY_TEMPERATURE_SYSTEM_STOPPED | 10 | Alarm! Too low supply temperature. System stopped. | 0:Not active, 1:Active | User | 2015-12-08
ALARM_TOO_HIGH_SUPPLY_TEMPERATURE_SYSTEM_STOPPED | 11 | Alarm! Too high supply temperature. System stopped. | 0:Not active, 1:Active | User | 2015-12-08
ALARM_CHANGE_SUPPLY_AIR_FILTER_PRESS_RELE_SYSTEM_STOPPED | 12 | Warning! Change supply air filter (pressure relay). | 0:Not active, 1:Active | User | 2015-12-16
ALARM_CHANGE_EXTRACT_AIR_FILTER_PRESS_RELE_SYSTEM_STOPPED | 13 | Warning! Change extract air filter (pressure relay). | 0:Not active, 1:Active | User | 2015-12-16
ALARM_CHANGE_SUPPLY_AND_EXTRACT_FILTERS | 14 | Warning! Change supply and extract filters (timeout) | 0:Not active, 1:Active | User | 2015-12-08
ALARM_F1_FUSE_FAILURE | 15 | Alarm! Power supply failure. Please, check F1 fuse. | 0:Not active, 1:Active | User | 2016-08-08
ALARM_SUPPLY_AIR_TEMPERATURE_SENSOR_FAILURE_EMERGENCY_RUN | 16 | Warning! Supply air temperature sensor failure. Emergency run. | 0:Not active, 1:Active | User | 2015-12-08
ALARM_EXTRACT_AIR_TEMPERATURE_SENSOR_FAILURE_EMERGENCY_RUN | 17 | Warning! Extract air temperature sensor failure. Emergency run. | 0:Not active, 1:Active | User | 2015-12-08
ALARM_EXHAUST_AIR_TEMPERATURE_SENSOR_FAILURE_EMERGENCY_RUN | 18 | Warning! Exhaust air temperature sensor failure. Emergency run. | 0:Not active, 1:Active | User | 2015-12-08
ALARM_OUTDOOR_AIR_TEMPERATURE_SENSOR_FAILURE_EMERGENCY_RUN | 19 | Warning! Outdoor air temperature sensor failure. Emergency run. | 0:Not active, 1:Active | User | 2017-04-27
ALARM_HYDRONIC_HEATER_WATER_TEMPERATURE_SENSOR_FAILURE_EMERGENCY_RUN | 20 | Warning! Hydronic heater water temperature sensor failure. Emergency run. | 0:Not active, 1:Active | User | 2015-12-08
ALARM_HYDRONIC_PREHEATER_WATER_TEMPERATURE_SENSOR_FAILURE_EMERGENCY_RUN | 21 | Warning! Hydronic pre-heater water temperature sensor failure. Emergency run. | 0:Not active, 1:Active | User | 2015-12-08
ALARM_HYDRONIC_COOLER_WATER_TEMPERATURE_SENSOR_FAILURE_EMERGENCY_RUN | 22 | Warning! Hydronic cooler water temperature sensor failure. Emergency run. | 0:Not active, 1:Active | User | 2015-12-08
ALARM_CONTROL_BOX_TEMPERATURE_SENSOR_FAILURE_EMERGENCY_RUN | 23 | Warning! Controller cabinet temperature sensor failure. Emergency run. | 0:Not active, 1:Active | User | 2015-12-08
ALARM_SUPPLY_AIR_TEMPERATURE_SENSOR_FAILURE_SYSTEM_STOPPED | 24 | Alarm! Supply air temperature sensor failure. System stopped. | 0:Not active, 1:Active | User | 2015-12-08
ALARM_EXTRACT_AIR_TEMPERATURE_SENSOR_FAILURE_SYSTEM_STOPPED | 25 | Alarm! Extract air temperature sensor failure. System stopped. | 0:Not active, 1:Active | User | 2015-12-08
ALARM_EXHAUST_AIR_TEMPERATURE_SENSOR_FAILURE_SYSTEM_STOPPED | 26 | Alarm! Exhaust air temperature sensor failure. System stopped. | 0:Not active, 1:Active | User | 2015-12-08
ALARM_OUTDOOR_AIR_TEMPERATURE_SENSOR_FAILURE_SYSTEM_STOPPED | 27 | Alarm! Outdoor air temperature sensor failure. System stopped. | 0:Not active, 1:Active | User | 2017-04-27
ALARM_HYDRONIC_HEATER_WATER_TEMPERATURE_SENSOR_FAILURE_SYSTEM_STOPPED | 28 | Alarm! Hydronic heater water temperature sensor failure. System stopped. | 0:Not active, 1:Active | User | 2015-12-08
ALARM_HYDRONIC_PREHEATER_WATER_TEMPERATURE_SENSOR_FAILURE_SYSTEM_STOPPED | 29 | Alarm! Hydronic pre-heater water temperature sensor failure. System stopped. | 0:Not active, 1:Active | User | 2015-12-08
ALARM_HYDRONIC_COOLER_WATER_TEMPERATURE_SENSOR_FAILURE_SYSTEM_STOPPED | 30 | Alarm! Hydronic cooler water temperature sensor failure. System stopped. | 0:Not active, 1:Active | User | 2015-12-08
ALARM_CONTROL_BOX_TEMPERATURE_SENSOR_FAILURE_SYSTEM_STOPPED | 31 | Alarm! Controller cabinet temperature sensor failure. System stopped. | 0:Not active, 1:Active | User | 2015-12-08
ALARM_FIRE_DAMPER_TEST_OK | 32 | Fire damper test OK | 0:Not active, 1:Active | User | 2015-12-08
ALARM_FIRE_DAMPER_TEST_FAILED | 33 | Warning! Fire damper test failed | 0:Not active, 1:Active | User | 2015-12-08
ALARM_HEATER_MANUAL_PROTECTION_SYSTEM_STOPPPED | 34 | Alarm! Heater manual protection. System stopped! | 0:Not active, 1:Active | User | 2015-12-08
ALARM_HEATER_AUTOMATIC_PROTECTION | 35 | Warning! Heater automatic protection | 0:Not active, 1:Active | User | 2015-12-08
ALARM_PREHEATER_MANUAL_PROTECTION_SYSTEM_STOPPPED | 36 | Alarm! Pre-heater manual protection. System stopped! | 0:Not active, 1:Active | User | 2015-12-08
ALARM_PREHEATER_AUTOMATIC_PROTECTION | 37 | Warning! Pre-heater automatic protection | 0:Not active, 1:Active | User | 2015-12-08
ALARM_SUPPLY_FAN_PROTECTION | 38 | Alarm! Supply fan failure | 0:Not active, 1:Active | User | 2015-12-08
ALARM_EXTRACT_FAN_PROTECTION | 39 | Alarm! Extract fan failure | 0:Not active, 1:Active | User | 2015-12-08
ALARM_DX_COOLER_PROTECTION | 40 | Alarm! DX cooler failure | 0:Not active, 1:Active | User | 2015-12-08
ALARM_FIRE_ALARM | 41 | Alarm! Fire | 0:Not active, 1:Active | User | 2015-12-08
ALARM_SUPPLY_FAN_PRESSURE_PROTECTION_SYSTEM_STOPPPED | 42 | Alarm! Supply fan pressure protection. System stopped. | 0:Not active, 1:Active | User | 2015-12-08
ALARM_EXTRACT_FAN_PRESSURE_PROTECTION_SYSTEM_STOPPPED | 43 | Alarm! Extract fan pressure protection. System stopped. | 0:Not active, 1:Active | User | 2015-12-08
ALARM_INTERNAL | 44 | Alarm! Internal system error. | 0:Not active, 1:Active | User | 2015-12-08
ALARM_HEATER_MANUAL_PROTECTION_BOOSTING | 45 | Alarm! Heater manual protection. Boosting. | 0:Not active, 1:Active | User | 2015-12-08
ALARM_PREHEATER_MANUAL_PROTECTION_BOOSTING | 46 | Alarm! Pre-heater manual protection. Boosting. | 0:Not active, 1:Active | User | 2015-12-08
ALARM_INTERNAL_COMMUNICATION_ERROR | 47 | Alarm! Internal communication error | 0:Not active, 1:Active | User | 2015-12-08
ALARM_DX_COOLER_DEFROSTING | 48 | Warning! DX cooler defrosting | 0:Not active, 1:Active | User | 2016-08-30
ALARM_TOO_HI_3DAYS_RH | 49 | Warning! Too high 3 days extract humidity. Increasing air flow. | 0:Not active, 1:Active | User | 2016-08-30
ALARM_TOO_HI_RH | 50 | Warning! Too high extract humidity. Boosting. | 0:Not active, 1:Active | User | 2016-08-30
ALARM_ROTOR_BROKEN_BELT_ALARM_SYSTEM_STOPPED | 51 | Alarm! Rotor broken belt alarm. System stopped. | 0:Not active, 1:Active | User | 2017-01-24
ALARM_GAS_HEATER_FAILURE | 52 | Warning! Gas heater failure | 0:Not active, 1:Active | User | 2017-04-27
ALARM_GAS_PREHEATER_FAILURE | 53 | Warning! Gas pre-heater failure | 0:Not active, 1:Active | User | 2017-04-27
ALARM_TOO_HI_CONDENSATION | 54 | Warning! Too high condensation level | 0:Not active, 1:Active | User | 2017-04-27
ALARM_SUPPLY_FAN_FAILURE_EMERGENCY_RUN | 55 | Warning! Supply fan failure. Emergency run. | 0:Not active, 1:Active | User | 2017-04-27
ALARM_EXTRACT_FAN_FAILURE_EMERGENCY_RUN | 56 | Warning! Extract fan failure. Emergency run. | 0:Not active, 1:Active | User | 2017-04-27
ALARM_TOO_LOW_SUPPLY_AIR_FLOW | 57 | Warning! Too low supply air flow for DX cooler | 0:Not active, 1:Active | User | 2017-09-18
ALARM_BYPASS_DAMPER_ALARM_SYSTEM_STOPPED | 58 | Alarm! Bypass damper failure. System stopped. | 0:Not active, 1:Active | User | 2018-03-01
ALARM_HEATER_CIRC_PUMP_FAILURE_SYSTEM_STOPPED | 59 | Alarm! Hydronic heater/pre-heater circ. pump failute. System stopped. | 0:Not active, 1:Active | User | 2018-03-01
ALARM_HEATER_CIRC_PUMP_FAILURE | 60 | Warning! Hydronic heater/pre-heater circ. pump failute. | 0:Not active, 1:Active | User | 2018-03-01
ALARM_REMOTE_HEATER_ALARM_SYSTEM_STOPPED | 61 | Alarm! Remote heater failure! | 0:Not active, 1:Active | User | 2018-05-02
ALARM_REMOTE_HEATER_WARNING | 62 | Warning! Remote heater failure! | 0:Not active, 1:Active | User | 2018-05-02
ALARM_REMOTE_PRE_HEATER_ALARM_SYSTEM_STOPPED | 63 | Alarm! Remote pre-heater failure! | 0:Not active, 1:Active | User | 2018-05-02
ALARM_REMOTE_PRE_HEATER_WARNING | 64 | Warning! Remote pre-heater failure! | 0:Not active, 1:Active | User | 2018-05-02
ALARM_REMOTE_COOLER_ALARM_SYSTEM_STOPPED | 65 | Alarm! Remote cooler failure! | 0:Not active, 1:Active | User | 2018-05-02
ALARM_REMOTE_COOLER_WARNING | 66 | Warning! Remote cooler failure! | 0:Not active, 1:Active | User | 2018-05-02
ALARM_FIRE_ALARM2 | 67 | Alarm! Fire protection 2 | 0:Not active, 1:Active | User | 2018-05-02
ALARM_REMOTE_HEATER_ALARM_BOOSTING | 68 | Warning! Remote heater failure! Boosting. | 0:Not active, 1:Active | User | 2019-09-21
ALARM_REMOTE_PRE_HEATER_ALARM_BOOSTING | 69 | Warning! Remote pre-heater failure! Boosting. | 0:Not active, 1:Active | User | 2019-09-21
ALARM_FIRE_DAMPER_FAILURE | 70 | Alarm! Fire damper failure | 0:Not active, 1:Active | User | 2019-09-21
| 71 | Warning! After heat exchanger temperature sensor failure. Emergency run. | 0:Not active, 1:Active | User | 2019-03-14
| 72 | Alarm! After heat exchanger temperature sensor failure. System stopped. | 0:Not active, 1:Active | User | 2019-03-14
Reserved
DI_CRITICAL_ALARM | 188 | Any active critical alarm | 0:Not active, 1:Active | User | 2015-12-08
DI_WARNING | 189 | Any active warning | 0:Not active, 1:Active | User | 2015-12-08
Test mode
DEFINE | Address | Name | Values | User level | Updated
DI_TESTMODE_HALL | 190 | IN TEST MODE: Hall sensor signal state | 0:Not active, 1:Active | User | 2015-07-20
DI_TESTMODE_FDI1 | 191 | IN TEST MODE: FDI1 signal state | 0:Not active, 1:Active | User | 2015-07-20
DI_TESTMODE_FDI2 | 192 | IN TEST MODE: FDI2 signal state | 0:Not active, 1:Active | User | 2015-07-10
Status
DEFINE | Address | Name | Values | User level | Updated
DI_REMOTE_MODE_SWITCH | 200 | DI1-Remote mode switch | 0:Not active, 1:Active | User | 2015-07-10
DI_REMOTE_CUSTOM_FANS_SPEED_SWITCH | 201 | DI2-Remote custom fans speed switch | 0:Not active, 1:Active | User | 2015-07-10
DI_WORKING_INDICATION_OUTPUT | 202 | TDO1-Working indication output | 0:Not active, 1:Active | User | 2015-07-10
DI_ALARM_INDICATION_OUTPUT | 203 | TDO2-Alarm indication output | 0:Not active, 1:Active | User | 2015-07-10
DI_SLOWING_DOWN_FANS_BY_TEMPERATURE | 204 | Slowing down fans by temperature | 0:Not active, 1:Active | User | 2015-07-10
DI_REDUCING_CO_LEVEL | 205 | Reducing CO2 level | 0:Not active, 1:Active | User | 2015-07-10
DI_HYDRONIC_PUMP_EXERCISE | 206 | Hydronic pump exercise | 0:Not active, 1:Active | User | 2015-12-08
DI_HEATING_SEASON | 207 | Winter | 0:Cooling, 1:Heating | User | 2015-12-10
DI_STANDBY_MODE_BLOCKING | 208 | Standby mode blocking | 0:Not active, 1:Active | User | 2015-07-10
DI_NIGHT_COOLING_FUNCTION | 209 | Night cooling function | 0:Not active, 1:Active | User | 2015-07-10
DI_SLOWING_DOWN_FANS | 210 | Slowing down fans | 0:Not active, 1:Active | User | 2015-07-10
DI_SERVICE_STOP_FUNCTION | 211 | Service stop function | 0:Not active, 1:Active | User | 2015-07-10
DI_SERVICE_HOLIDAYS | 212 | Holidays indication | 0:Not active, 1:Active | User | 2015-07-10
DI_FULL_RECIRCULATION | 213 | Full recirculation function | 0:Not active, 1:Active | User | 2015-11-09
DI_POOL_FUNCTION | 214 | Pool function | 0:Not active, 1:Active | User | 2017-11-29
DI_LOST_PERIFERIA_POWER_SUPPLY | 215 | No power indication | 0:Not active, 1:Active | User | 2018-03-01
Reserved
DI_HEATER_POWER_LINE_CIRCULATION_PUMP | 300 | DO1-Heater power line/circulation pump | 0:Not active, 1:Active | Adjuster | 2015-07-10
DI_HEATER_MANUAL_PROTECTION | 301 | DI3-Heater manual protection | 0:Not active, 1:Active | Adjuster | 2015-07-10
DI_HEATER_AUTOMATIC_PROTECTION | 302 | DI4-Heater automatic protection | 0:Not active, 1:Active | Adjuster | 2015-07-10
DI_PREHEATER_POWER_LINE_CIRCULATION_PUMP | 303 | DO2-Pre-heater power line/circulation pump | 0:Not active, 1:Active | Adjuster | 2015-07-10
DI_PREHEATER_MANUAL_PROTECTION | 304 | DI5-Pre-heater manual protection | 0:Not active, 1:Active | Adjuster | 2015-07-10
DI_PREHEATER_AUTOMATIC_PROTECTION | 305 | DI6-Pre-heater automatic protection | 0:Not active, 1:Active | Adjuster | 2015-07-10
DI_SUPPLY_FAN_PROTECTION | 306 | DI7-Supply fan protection | 0:Not active, 1:Active | Adjuster | 2015-07-10
DI_EXTRACT_FAN_PROTECTION | 307 | DI8-Extract fan protection | 0:Not active, 1:Active | Adjuster | 2015-07-10
DI_FANS_POWER_LINE | 308 | DO3-Fans power line | 0:Not active, 1:Active | Adjuster | 2015-07-10
DI_HX_PRESS_RELAY | 309 | DI9-Heat exchanger pressure relay | 0:Not active, 1:Active | Adjuster | 2015-11-09
DI_BYPASS_CLOSED | 310 | DI10-Bypass closed | 0:Not active, 1:Active | Adjuster | 2015-07-10
DI_BYPASS_OPEN_OUTPUT | 311 | DO4-Bypass open output | 0:Not active, 1:Active | Adjuster | 2015-07-10
DI_BYPASS_CLOSE_OUTPUT | 312 | DO5-Bypass close output | 0:Not active, 1:Active | Adjuster | 2015-07-10
DI_ROTOR_ON | 313 | DO6-Rotor ON | 0:Not active, 1:Active | Adjuster | 2015-07-10
DI_DX_COOLER_REVERSE | 314 | DX cooler reverse | 0:Not active, 1:Active | Adjuster | 2016-01-07
DI_DX_COOLER_PROTECTION | 315 | DX cooler protection | 0:Not active, 1:Active | Adjuster | 2015-07-10
DI_DX_COOLER_POWER_LINE | 316 | DX cooler power line | 0:Not active, 1:Active | Adjuster | 2017-02-01
DI_HYDRONIC_COOLER_CIRCULATION_PUMP | 317 | DO9-Hydronic cooler circulation pump | 0:Not active, 1:Active | Adjuster | 2015-12-08
DI_FIRE_PROTECTION_INPUT | 318 | DI11-Fire protection input | 0:Not active, 1:Active | Adjuster | 2015-07-10
DI_FIRE_DAMPER_OPENED | 319 | DI12-Fire damper opened | 0:Not active, 1:Active | Adjuster | 2015-07-10
DI_FIRE_DAMPER_CLOSED | 320 | DI13-Fire damper closed | 0:Not active, 1:Active | Adjuster | 2015-07-10
DI_FIRE_DAMPER_OPEN_OUTPUT | 321 | DO10-Fire damper open output | 0:Not active, 1:Active | Adjuster | 2015-07-10
DI_FIRE_DAMPER_CLOSE_OUTPUT | 322 | DO11-Fire damper close output | 0:Not active, 1:Active | Adjuster | 2015-07-10
DI_SUPPLY_RECIRCULATION_DAMPER_OPEN_OUTPUT | 323 | DO12-Supply recirculation damper open output | 0:Not active, 1:Active | Adjuster | 2017-11-29
DI_SUPPLY_RECIRCULATION_DAMPER_CLOSE_OUTPUT | 324 | DO13-Supply recirculation damper close output | 0:Not active, 1:Active | Adjuster | 2017-11-29
DI_EXTRACT_DAMPER_OPEN_OUTPUT | 325 | DO14-Extract air damper open output | 0:Not active, 1:Active | Adjuster | 2018-03-28
DI_EXTRACT_DAMPER_CLOSE_OUTPUT | 326 | DO15-Extract air damper close output | 0:Not active, 1:Active | Adjuster | 2018-03-28
DI_SUPPLY_FILTER_PRESS_RELE | 327 | DI14-Supply filter pressure relay | 0:Not active, 1:Active | Adjuster | 2015-12-16
DI_EXTRACT_FILTER_PRESS_RELE | 328 | DI15-Extract filter pressure relay | 0:Not active, 1:Active | Adjuster | 2015-12-16
DI_CONTROL_BOX_HEATER_OUTPUT | 329 | DO16-Controller cabinet heater/fan output | 0:Not active, 1:Active | Adjuster | 2017-02-01
DI_SUPPLY_AIR_TEMPERATURE_SENSOR_FAILURE | 330 | Supply air temperature sensor FAILURE | 0:Failure, 1:OK | Adjuster | 2015-07-10
DI_EXTRACT_AIR_TEMPERATURE_SENSOR_ FAILURE | 331 | Extract air temperature sensor FAILURE | 0:Failure, 1:OK | Adjuster | 2015-07-10
DI_EXHAUST_AIR_TEMPERATURE_SENSOR_FAILURE | 332 | Exhaust air temperature sensor FAILURE | 0:Failure, 1:OK | Adjuster | 2015-07-10
DI_OUTDOOR_AIR_TEMPERATURE_SENSOR_FAILURE | 333 | Outdoor air temperature sensor FAILURE | 0:Failure, 1:OK | Adjuster | 2017-04-27
DI_HYDRONIC_HEATER_WATER_TEMPERATURE_SENSOR_FAILURE | 334 | Hydronic heater water temperature sensor FAILURE | 0:Failure, 1:OK | Adjuster | 2015-12-08
DI_HYDRONIC_PREHEATER_WATER_TEMPERATURE_SENSOR_FAILURE | 335 | Hydronic pre-heater water temperature sensor FAILURE | 0:Failure, 1:OK | Adjuster | 2015-12-08
DI_HYDRONIC_COOLER_WATER_TEMPERATURE_SENSOR_FAILURE | 336 | Hydronic cooler water temperature sensor FAILURE | 0:Failure, 1:OK | Adjuster | 2015-12-08
DI_CONTROL_BOX_TEMPERATURE_SENSOR_FAILURE | 337 | Controller cabinet temperature sensor FAILURE | 0:Failure, 1:OK | Adjuster | 2015-12-08
DI_RESERVED_TEMPERATURE_SENSOR_FAILURE | 338 | After heat excahnger temperature sensor FAILURE | 0:Failure, 1:OK | Adjuster | 2015-07-10
DI_FIRE_DAMPER_TESTING | 339 | Fire damper testing | 0: Not active, 1:Active | Adjuster | 2015-07-10
DI_RECIRCULATION_CLOSED | 340 | Circulation damper closed | 0: Not active, 1:Active | Adjuster | 2015-07-10
DI_FIRE_PLACE_PROTECTION_INPUT | 341 | Fire place protection relay input | 0: Not active, 1:Active | Adjuster | 2015-07-10
DI_DX_COOLER_DEFROST_INPUT | 342 | DX cooler defrost input | 0: Not active, 1:Active | Adjuster | 2016-08-30
DI_HX_DAMPER_1 | 343 | Heatexchanger segment damper I | 0: Not active, 1:Active | Adjuster | 2016-08-30
DI_HX_DAMPER_2 | 344 | Heatexchanger segment damper II | 0: Not active, 1:Active | Adjuster | 2016-08-30
DI_HX_DAMPER_3 | 345 | Heatexchanger segment damper III | 0: Not active, 1:Active | Adjuster | 2016-08-30
DI_HCOOLER_CHANGEOVER_INPUT | 346 | Hydronic cooler changeover input | 0: Not active, 1:Active | Adjuster | 2016-08-30
DI_HCOOLER_HEATING | 347 | Hydronic cooler heating mode | 0: Not active, 1:Active | Adjuster | 2016-08-30
DI_TOO_HI_CONDENSATION | 348 | High condensation level input | 0: Not active, 1:Active | Adjuster | 2017-04-27
DI_SUPPLY_FAN_WARNING | 349 | Supply fan warning input | 0: Not active, 1:Active | Adjuster | 2017-04-27
DI_EXTRACT_FAN_WARNING | 350 | Extract fan warning input | 0: Not active, 1:Active | Adjuster | 2017-04-27
DI_DX_COOLER_DEFROST_OUTPUT | 351 | DX cooler defrost output | 0: Not active, 1:Active | Adjuster | 2017-09-18
DI_OUTSIDE_RECIRCULATION_DAMPER_OPEN_OUTPUT | 352 | Outside recirculation damper open output | 0:Not active, 1:Active | Adjuster | 2017-11-29
DI_OUTSIDE_RECIRCULATION_DAMPER_CLOSE_OUTPUT | 353 | Outside recirculation damper close output | 0:Not active, 1:Active | Adjuster | 2017-11-29
DI_HEATER_CIRC_PUMP_PROTECTION_INPUT | 354 | Heater circ. pump protection | 0:Not active, 1:Active | Adjuster | 2018-03-01
DI_PRE_HEATER_CIRC_PUMP_PROTECTION_INPUT | 355 | Pre-heater circ. pump protection | 0:Not active, 1:Active | Adjuster | 2018-03-01
DI_SUPPLY_DAMPER_OPEN_OUTPUT | 356 | Supply air damper open output | 0:Not active, 1:Active | Adjuster | 2018-03-28
DI_SUPPLY_DAMPER_CLOSE_OUTPUT | 357 | Supply air damper close output | 0:Not active, 1:Active | Adjuster | 2018-03-28
DI_COOKERHOOD_DAMPER_OPEN_OUTPUT | 358 | CookerHood damper open output | 0:Not active, 1:Active | Adjuster | 2026-04-22
DI_COOKERHOOD_DAMPER_CLOSE_OUTPUT | 359 | CookerHood damper close output | 0:Not active, 1:Active | Adjuster | 2026-04-22
DI_COOKERHOOD_DAMPER_LIGHTING_OUTPUT | 360 | CookerHood lighting output | 0:Not active, 1:Active | Adjuster | 2026-04-22
DI_NOT_USED | 361 | Not used | 0:Not active, 1:Active | Adjuster | 2026-04-22
DI_NOT_USED | 362 | Not used | 0:Not active, 1:Active | Adjuster | 2026-04-22
DI_NOT_USED | 363 | Not used | 0:Not active, 1:Active | Adjuster | 2026-04-22
DI_NOT_USED | 364 | Not used | 0:Not active, 1:Active | Adjuster | 2026-04-22
DI_FIRE_PROTECTION2_INPUT | 365 | Fire protection 2 input | 0:Not active, 1:Active | Adjuster | 2018-05-03

## Input register
Input register 0x04, Read only
DEFINE | Address | Name | Values | User level | Updated
IR_CURRENT_SYSTEM_STATE | 1 | Current system state | 0-255 | User | 2015-07-10
IR_SOFTWARE_VERSION | 2 | Software version | - | User | 2015-07-10
IR_CONFIGURATION_VERSION | 3 | Configuration version | - | User | 2015-07-10
IR_YEARS | 4 | Years | 0..99 | User | 2017-04-28
IR_MONTH | 5 | Month | 1..12 | User | 2015-07-10
IR_DAY | 6 | Day | 1..31 | User | 2015-07-10
IR_WEEK_DAY | 7 | Week day | 1..7 | User | 2015-07-10
IR_HOURS | 8 | Hours | 0..23 | User | 2015-07-10
IR_MINUTES | 9 | Minutes | 0..59 | User | 2015-07-10
IR_SECONDS | 10 | Seconds | 0..59 | User | 2015-07-10
IR_WORKING_DAYS | 11 | Working days |  | User | 2015-07-10
IR_WORKING_HOURS | 12 | Working Hours | 0-23h | User | 2015-07-10
IR_INTENSIVE_AIR_FLOW_TIME_LEFT | 13 | Intensive air flow time left | 0-36000 s | User | 2015-07-10
IR_STANDBY_BLOCKING_TIME_LEFT_THIS_DAY | 14 | Standby blocking time left this day | 0-500 min. | User | 2015-07-10
IR_CURRENT_SYSTEM_MODE | 15 | Current system mode | 0-4 | User | 2015-07-10
IR_CURRENT_AIR_FLOW | 16 | Current air flow | 0..100% | User | 2015-07-10
IR_REQUIRED_SUPPLY_TEMPERATURE | 17 | Required supply temperature | Value*0,1 °C | User | 2015-07-10
IR_SUPPLY_AIR_TEMPERATURE | 18 | T1-Supply air temperature | Value*0,1 °C | User | 2015-07-10
IR_EXTRACT_AIR_TEMPERATURE | 19 | T2-Extract air temperature | Value*0,1 °C | User | 2015-07-10
IR_EXHAUST_AIR_TEMPERATURE | 20 | T3-Exhaust air temperature | Value*0,1 °C | User | 2015-07-10
IR_OUTDOOR_AIR_TEMPERATURE | 21 | T4-Outdoor air temperature | Value*0,1 °C | User | 2017-04-27
IR_AIR_SUPPLY_AIR_RH | 22 | A1-Supply air RH | (0-1000)*0,1 % | User | 2015-07-10
IR_AIR_SUPPLY_AIR_CO2 | 23 | A1-Supply air CO2 | 0-2000 ppm | User | 2015-07-10
IR_AIR_EXTRACT_AIR_RH | 24 | A2-Extract air RH | (0-1000)*0,1 % | User | 2015-07-10
IR_AIR_EXTRACT_AIR_CO2 | 25 | A2-Extract air CO2 | 0-2000 ppm | User | 2015-07-10
IR_TIME_TO_NEXT_SCHEDULER_EVENT_HOURS | 26 | Time to next scheduler event (hours) 0-less than hour, 24-more than day | 0-24 | User | 2015-07-10
IR_TIME_TO_NEXT_SCHEDULER_EVENT_MINUTES | 27 | Time to next scheduler event (minutes) 0-less than minute | 0-60 | User | 2015-07-10
IR_ACTIVE_ALARMS_COUNT | 28 | Active alarms count | 0-100 | User | 2015-07-10
Reserverd
IR_FILTERS_TIMER_DAYS_LEFT | 30 | Filters timer days left | 1 - 365 (days) | User | 2015-07-10
IR_BOOTLOADER_VERSION | 31 | Bootloader version | - | Adjuster | 2016-05-12
IR_HX_PRESSURE | 32 | Heatexchanger pressure | 0-3000Pa | Adjuster | 2016-08-30
IR_EX1_MODULE | 50 | EX1 Module | - | Adjuster | 2015-07-10
IR_EX2_MODULE | 51 | EX2 Module | - | Adjuster | 2015-07-10
IR_COMUNICATION_MODULE | 52 | Comunication Module | - | Adjuster | 2015-07-10
| 53 | Reserverd
IR_SUPPLY_FAN_SPREED_RPM | 55 | Supply fan spreed RPM | 0 - 5000 RPM | Adjuster | 2015-07-10
IR_EXTRACT_FAN_SPREED_RPM | 56 | Extract fan spreed RPM | 0 - 5000 RPM | Adjuster | 2015-07-10
IR_CURRENT_SUPPLY_AIR_FAN_OUTPUT | 57 | AO1-Current supply air fan output (Volts) | 0..1000 *0.01 Volts | Adjuster | 2015-07-10
IR_CURRENT_SUPPLY_AIR_FLOW | 58 | Current supply air flow (%) | 0..1000 *0.1 % | Adjuster | 2015-07-10
IR_CURRENT_SUPPLY_AIR_DUCT_PRESSURE | 59 | Current supply air duct pressure (Pa) | 0..30000 Pa (if C141 == 0, *0.1) | Adjuster | 2018-10-18
IR_CURRENT_SUPPLY_AIR_FLOW_M_H | 60 | Current supply air flow (m3/h) | 0..30000 m3/h | Adjuster | 2017-04-27
IR_CURRENT_EXTRACT_AIR_FAN_OUTPUT | 61 | AO2-Current extract air fan output (V) | 0..1000 *0.01 Volts | Adjuster | 2015-07-10
IR_CURRENT_EXTRACT_AIR_FLOW | 62 | Current extract air flow (%) | 0..1000 *0.1 % | Adjuster | 2015-07-10
IR_CURRENT_EXTRACT_AIR_DUCT_PRESSURE | 63 | Current extract air duct pressure (Pa) | 0..30000 Pa (if C141 == 0, *0.1) | Adjuster | 2018-10-18
IR_CURRENT_EXTRACT_AIR_FLOW | 64 | Current extract air flow (m3/h) | 0..30000 m3/h | Adjuster | 2017-04-27
IR_1_SUPPLY_AIR_FLOW_FLOW_PRESSURE | 65 | 1 Supply air flow pressure (Pa) | 0..30000 Pa | Adjuster | 2017-04-27
IR_2_SUPPLY_AIR_FLOW_FLOW_PRESSURE | 66 | 2 Supply air flow pressure (Pa) | 0..30000 Pa | Adjuster | 2017-04-27
IR_3_SUPPLY_AIR_FLOW_FLOW_PRESSURE | 67 | 3 Supply air flow pressure(Pa) | 0..30000 Pa | Adjuster | 2017-04-27
IR_4_SUPPLY_AIR_FLOW_FLOW_PRESSURE | 68 | 4 Supply air flow pressure(Pa) | 0..30000 Pa | Adjuster | 2017-04-27
| 69 | Reserved
IR_1_EXTRACT_AIR_FLOW_FLOW_PRESSURE | 71 | 1 Extract air flow pressure (Pa) | 0..30000 Pa | Adjuster | 2017-04-27
IR_2_EXTRACT_AIR_FLOW_FLOW_PRESSURE | 72 | 2 Extract air flow pressure (Pa) | 0..30000 Pa | Adjuster | 2017-04-27
IR_3_EXTRACT_AIR_FLOW_FLOW_PRESSURE | 73 | 3 Extract air flow pressure(Pa) | 0..30000 Pa | Adjuster | 2017-04-27
IR_4_EXTRACT_AIR_FLOW_FLOW_PRESSURE | 74 | 4 Extract air flow pressure(Pa) | 0..30000 Pa | Adjuster | 2017-04-27
| 75 | Reserved
IR_1_SUPPLY_AIR_FLOW_FLOW | 77 | 1 Supply air flow (m3/h) | 0..30000 m3/h | Adjuster | 2017-04-27
IR_2_SUPPLY_AIR_FLOW_FLOW | 78 | 2 Supply air flow (m3/h) | 0..30000 m3/h | Adjuster | 2017-04-27
IR_3_SUPPLY_AIR_FLOW_FLOW | 79 | 3 Supply air flow (m3/h) | 0..30000 m3/h | Adjuster | 2017-04-27
IR_4_SUPPLY_AIR_FLOW_FLOW | 80 | 4 Supply air flow (m3/h) | 0..30000 m3/h | Adjuster | 2017-04-27
| 81 | Reserved
IR_1_EXTRACT_AIR_FLOW_FLOW | 83 | 1 Extract air flow (m3/h) | 0..30000 m3/h | Adjuster | 2017-04-27
IR_2_EXTRACT_AIR_FLOW_FLOW | 84 | 2 Extract air flow (m3/h) | 0..30000 m3/h | Adjuster | 2017-04-27
IR_3_EXTRACT_AIR_FLOW_FLOW | 85 | 3 Extract air flow (m3/h) | 0..30000 m3/h | Adjuster | 2017-04-27
IR_4_EXTRACT_AIR_FLOW_FLOW | 86 | 4 Extract air flow (m3/h) | 0..30000 m3/h | Adjuster | 2017-04-27
| 87 | Reserved
IR_HEATER_CONTROL_OUTPUT | 89 | AO3-Heater control output | (0-1000)*0,1 % | Adjuster | 2015-07-10
IR_HYDRONIC_HEATER_WATER_TEMPERATURE | 90 | T5-Hydronic heater water temperature | Value*0,1 °C | Adjuster | 2015-12-08
IR_PREATER_CONTROL_OUTPUT | 91 | AO4-Preater control output | (0-1000)*0,1 % | Adjuster | 2015-07-10
IR_HYDRONIC_PREHEATER_WATER_TEMPERATURE | 92 | T6-Hydronic pre-heater water temperature | Value*0,1 °C | Adjuster | 2015-12-08
IR_BYPASS_POSITION | 93 | Bypass position | (0-1000)*0,1 % | Adjuster | 2015-07-10
IR_ROTOR_SPEED_RPM | 94 | Rotor speed RPM | 0-100 RPM | Adjuster | 2015-07-10
IR_ROTOR_CONTROL_OUTPUT | 95 | AO5-Rotor control output | (0-1000)*0,1 % | Adjuster | 2015-07-10
IR_HYDRONIC_COOLER_WATER_TEMPERATURE | 96 | T7-Hydronic cooler water temperature | Value*0,1 °C | Adjuster | 2015-12-08
IR_HYDRONIC_COOLER_CONTROL_OUTPUT | 97 | AO6-Hydronic cooler control output | (0-1000)*0,1 % | Adjuster | 2015-12-08
IR_FIRE_DAMPER_POSITION | 98 | Fire damper position | (0-1000)*0,1 % | Adjuster | 2015-07-10
IR_FIRE_DAMPER_TESTING_PROGRESS | 99 | Fire damper testing progress | 0..100% | Adjuster | 2015-07-10
IR_SUPPLY_RECIRCULATION_DAMPER_POSITION | 100 | Supply recirculation damper position | (0-1000)*0,1 % | Adjuster | 2017-11-29
IR_EXTRACT_DAMPER_POSITION | 101 | Extract air damper position | (0-1000)*0,1 % | Adjuster | 2018-03-28
IR_CONTROL_BOX_TEMPERATURE | 102 | T8-Controller cabinet temperature | Value*0,1 °C | Adjuster | 2015-12-08
IR_FROST_POINT | 103 | Frost point | Value*0,1 °C | Adjuster | 2015-07-10
IR_HEATEXCHANGER_TEMPERATURE | 104 | Heater exchanger temp | Value*0,1 °C | Adjuster | 2015-07-10
IR_DX_COOLER_CONTROL_OUTPUT | 105 | DX cooler control output | (0-1000)*0,1 % | Adjuster | 2016-01-07
IR_ACTIVE_ACCESS_LEVEL | 106 | Active access level | 1-Adjuster, 2-Service |  | 2015-07-10
IR_AHU_ID_1 | 107 | AHU ID 1 | 0-9999 | Adjuster | 2015-10-27
IR_AHU_ID_2 | 108 | AHU ID 2 | 0-9999 | Adjuster | 2015-10-27
IR_AHU_ID_3 | 109 | AHU ID 3 | 0-9999 | Adjuster | 2015-10-27
IR_AHU_ID_4 | 110 | AHU ID 4 | 0-9999 | Adjuster | 2015-10-27
IR_AHU_ID_5 | 111 | AHU ID 5 | 0-9999 | Adjuster | 2015-10-27
IR_SUPPLY_FILTER_PRESSURE | 112 | Supply air filter pressure | 0..30000 Pa | Adjuster | 2017-04-27
IR_SUPPLY_FILTER_PRESSURE_ON_LIMIT | 113 | Supply air filter pressure ON limit | 0..30000 Pa | Adjuster | 2017-04-27
IR_SUPPLY_FILTER_PRESSURE_OFF_LIMIT | 114 | Supply air filter pressure OFF limit | 0..30000 Pa | Adjuster | 2017-04-27
IR_EXTRACT_FILTER_PRESSURE | 115 | Extraxt air filter pressure | 0..30000 Pa | Adjuster | 2017-04-27
IR_EXTRACT_FILTER_PRESSURE_ON_LIMIT | 116 | Extraxt air filter pressure ON limit | 0..30000 Pa | Adjuster | 2017-04-27
IR_EXTRACT_FILTER_PRESSURE_OFF_LIMIT | 117 | Extraxt air filter pressure OFF limit | 0..30000 Pa | Adjuster | 2017-04-27
IR_HEAT_EXCHANGER_PRESSURE | 118 | Heat exchanger pressure | 0..30000 Pa | Adjuster | 2017-04-27
IR_HEAT_EXCHANGER_PRESSURE_ON_LIMIT | 119 | Heat exchanger pressure ON limit | 0..30000 Pa | Adjuster | 2017-04-27
IR_HEAT_EXCHANGER_PRESSURE_OFF_LIMIT | 120 | Heat exchanger pressure OFF limit | 0..30000 Pa | Adjuster | 2017-04-27
IR_DX_COIL_PRESSURE | 121 | DX Cooler coil pressure | 0..30000 Pa | Adjuster | 2017-04-27
IR_DX_COIL_PRESSURE_ON_LIMIT | 122 | DX Cooler coil pressure ON limit | 0..30000 Pa | Adjuster | 2017-04-27
IR_DX_COIL_PRESSURE_OFF_LIMIT | 123 | DX Cooler coil pressure OFF limit | 0..30000 Pa | Adjuster | 2017-04-27
IR_AFTER_HX_TEMPERATURE | 124 | After heat exchanger temperature | Value*0,1 °C | Adjuster | 2017-09-18
IR_TEMP_TRANSFER_EFFICIENCY | 125 | Heat transfer efficiency | 0-100% | Adjuster | 2017-09-18
IR_OUTSIDE_RECIRCULATION_DAMPER_POSITION | 126 | Outside recirculation damper position | (0-1000)*0,1 % | Adjuster | 2017-09-18
IR_POOL_FUNCTION_MODE | 127 | Pool function mode | Value*0,1 | Adjuster | 2017-11-29
IR_SUPPLY_DAMPER_POSITION | 128 | Supply air damper position | (0-1000)*0,1 % | Adjuster | 2018-03-28
IR_CURRENT_SUPPLY_AIR_FLOW_PRESSURE2 | 129 | Current supply air flow pressure 2 (Pa) | 0..30000 Pa (if > 0) | Adjuster | 2018-03-28
IR_CURRENT_EXTRACT_AIR_FLOW_PRESSURE2 | 130 | Current extract air flow pressure 2 (Pa) | 0..30000 Pa (if > 0) | Adjuster | 2018-03-28
IR_PRE_HEATING_AIR_SETPOINT | 131 | Preheating air setpoint | Value*0,1 °C | Adjuster | 2018-05-02
IR_PRE_HEATING_AIR_TEMPERATURE | 132 | Preheating air temperature | Value*0,1 °C | Adjuster | 2018-05-02

## System state
System state
ID | Message | Priority | Updated
0 | Stand-by | 0 | 2015-07-10
1 | Building protection | 0 | 2017-09-18
2 | Economy | 0 | 2015-07-10
3 | Comfort | 0 | 2017-09-18
4 | Emergency run | 2 | 2015-07-10
5 | Preparing | 7 | 2015-07-10
6 | Opening dampers | 7 | 2015-07-10
7 | Boost | 6 | 2015-07-10
8 | Cooling heaters | 7 | 2015-07-10
9 | Closing dampers | 7 | 2015-07-10
10 | Night Cooling | 7 | 2015-12-16
11 | Critical alarm | 4 | 2015-07-10
12 | Fire alarm | 5 | 2015-07-10
13 | Heat exchanger frost protection | 3 | 2015-07-10
14 | Change filters | 1 | 2015-07-10
15 | Room RH 3 days average is lower than 30%. Limiting speed. | 1 | 2017-12-20
16 | DX cooler defrosting | 1 | 2017-12-20
17 | Fire damper testing | 1 | 2017-12-20

## Alarm list
Alarm list
S-touch CODE | Modbus CODE | Message
| 0 | -------------- | Updated
W.01 | 1 | Warning! Rotor broken belt alarm | 2015-12-08
A.02 | 2 | Alarm! Fireplace protection activated | 2015-12-08
W.03 | 3 | Warning! Dryness protection activated | 2015-12-08
W.04 | 4 | Warning! Plate heat exchanger frost protection activated | 2015-12-08
A.05 | 5 | Alarm! Frost protection. System stopped. | 2016-05-09
W.06 | 6 | Warning! Plate heat exchanger frost protection (pressure relay) | 2015-12-16
A.07 | 7 | Alarm! Hydronic heater frost protection. System stopped. | 2015-12-08
W.08 | 8 | Warning! Too low supply temperature | 2015-12-08
W.09 | 9 | Warning! Too high supply temperature | 2015-12-08
A.10 | 10 | Alarm! Too low supply temperature. System stopped. | 2015-12-08
A.11 | 11 | Alarm! Too high supply temperature. System stopped. | 2015-12-08
W.12 | 12 | Warning! Change supply air filter (pressure relay). | 2015-12-16
W.13 | 13 | Warning! Change extract air filter (pressure relay). | 2015-12-16
W.14 | 14 | Warning! Change supply and extract filters (timeout) | 2015-12-08
A.15 | 15 | Alarm! Power supply failure. Please, check F1 fuse. | 2016-08-08
W.16 | 16 | Warning! Supply air temperature sensor failure. Emergency run. | 2015-12-08
W.17 | 17 | Warning! Extract air temperature sensor failure. Emergency run. | 2015-12-08
W.18 | 18 | Warning! Exhaust air temperature sensor failure. Emergency run. | 2015-12-08
W.19 | 19 | Warning! Outdoor air temperature sensor failure. Emergency run. | 2017-04-27
W.20 | 20 | Warning! Hydronic heater water temperature sensor failure. Emergency run. | 2015-12-08
W.21 | 21 | Warning! Hydronic pre-heater water temperature sensor failure. Emergency run. | 2015-12-08
W.22 | 22 | Warning! Hydronic cooler water temperature sensor failure. Emergency run. | 2015-12-08
W.23 | 23 | Warning! Controller cabinet temperature sensor failure. Emergency run. | 2015-12-08
A.24 | 24 | Alarm! Supply air temperature sensor failure. System stopped. | 2015-12-08
A.25 | 25 | Alarm! Extract air temperature sensor failure. System stopped. | 2015-12-08
A.26 | 26 | Alarm! Exhaust air temperature sensor failure. System stopped. | 2015-12-08
A.27 | 27 | Alarm! Outdoor air temperature sensor failure. System stopped. | 2017-04-27
A.28 | 28 | Alarm! Hydronic heater water temperature sensor failure. System stopped. | 2015-12-08
A.29 | 29 | Alarm! Hydronic pre-heater water temperature sensor failure. System stopped. | 2015-12-08
A.30 | 30 | Alarm! Hydronic cooler water temperature sensor failure. System stopped. | 2015-12-08
A.31 | 31 | Alarm! Controller cabinet temperature sensor failure. System stopped. | 2015-12-08
F.32 | 32 | Fire damper test OK | 2015-12-08
W.33 | 33 | Warning! Fire damper test failed | 2015-12-08
A.34 | 34 | Alarm! Heater manual protection. System stopped! | 2015-12-08
W.35 | 35 | Warning! Heater automatic protection | 2015-12-08
A.36 | 36 | Alarm! Pre-heater manual protection. System stopped! | 2015-12-08
W.37 | 37 | Warning! Pre-heater automatic protection | 2015-12-08
A.38 | 38 | Alarm! Supply fan failure | 2015-12-08
A.39 | 39 | Alarm! Extract fan failure | 2015-12-08
W.40 | 40 | Warning! DX cooler failure | 2016-01-07
A.41 | 41 | Alarm! Fire | 2015-12-08
A.42 | 42 | Alarm! Supply fan pressure protection. System stopped. | 2015-12-08
A.43 | 43 | Alarm! Extract fan pressure protection. System stopped. | 2015-12-08
A.44 | 44 | Alarm! Internal system error. | 2015-12-08
A.45 | 45 | Alarm! Heater manual protection. Boosting. | 2015-12-08
A.46 | 46 | Alarm! Pre-heater manual protection. Boosting. | 2015-12-08
A.47 | 47 | Alarm! Internal communication error | 2015-12-08
W.48 | 48 | Warning! DX cooler defrosting | 2016-08-30
W.49 | 49 | Warning! Too high 3 days extract humidity. Increasing air flow. | 2016-08-30
W.50 | 50 | Warning! Too high extract humidity. Boosting. | 2016-08-30
A.51 | 51 | Alarm! Rotor broken belt alarm. System stopped. | 2017-01-24
W.52 | 52 | Warning! Gas heater failure | 2017-01-24
W.53 | 53 | Warning! Gas pre-heater failure | 2017-01-24
W.54 | 54 | Warning! Too high condensation level | 2017-01-24
W.55 | 55 | Warning! Supply fan failure. Emergency run. | 2017-01-24
W.56 | 56 | Warning! Extract fan failure. Emergency run. | 2017-01-24
W.57 | 57 | Warning! Too low supply air flow for DX cooler | 2017-09-18
A.58 | 58 | Alarm! Bypass damper failure. System stopped. | 2018-03-01
A.59 | 59 | Alarm! Hydronic heater/pre-heater circ. pump failute. System stopped. | 2018-03-01
W.60 | 60 | Warning! Hydronic heater/pre-heater circ. pump failute. | 2018-03-01
A.61 | 61 | Alarm! Remote heater failure! | 2018-05-03
W.62 | 62 | Warning! Remote heater failure! | 2018-05-03
A.63 | 63 | Alarm! Remote pre-heater failure! | 2018-05-03
W.64 | 64 | Warning! Remote pre-heater failure! | 2018-05-03
A.65 | 65 | Alarm! Remote cooler failure! | 2018-05-03
W.66 | 66 | Warning! Remote cooler failure! | 2018-05-03
A.67 | 67 | Alarm! Fire protection 2 | 2018-05-03
W.68 | 68 | Warning! Remote heater failure! Boosting. | 2018-09-21
W.69 | 69 | Warning! Remote pre-heater failure! Boosting. | 2018-09-21
A.70 | 70 | Alarm! Fire damper failure | 2018-09-21
W.71 | 71 | Warning! After heat exchanger temperature sensor failure. Emergency run. | 2019-03-14
A.72 | 72 | Alarm! After heat exchanger temperature sensor failure. System stopped. | 2019-03-14